## Lemont Outfall 2011
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg Sol | *Low Level Hg | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | ng/L | mg/L
2011-01-01 | 4.26 | 7.1 | 9.7 | N/S | N/S | N/S | <8 | <8 | 1326 | 166 | 1.62 | <0.25 | 8.96 | 0.77 | N/S | N/S | N/S | N/S | <0.04 | 0.035 | <0.001 | <0.002 | 0.0064 | 0.08 | N/S | <0.02 | 0.005 | N/S | <0.003 | <0.005 | <0.003 | 0.03 | <0.03 | <0.002 | <0.1 | N/S | 80.34 | 29.77 | 323 | N/S | N/S | N/S
2011-01-02 | 4.12 | 7.1 | 9.5 | 8 | 3 | N/S | 10 | <8 | 1407 | 166 | 2.46 | 0.53 | 11.24 | 0.97 | N/S | N/S | N/S | N/S | <0.04 | 0.0392 | <0.001 | <0.002 | 0.007 | 0.16 | N/S | <0.02 | 0.0081 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 85.36 | 32.01 | 345 | N/S | N/S | N/S
2011-01-03 | 3.29 | 7 | 7.5 | 8 | 3 | <2 | <8 | <8 | 1474 | 174 | 2.36 | 0.7 | 11.74 | 1.1 | 0.006 | 8 | 0.64 | 4600 | <0.04 | 0.0451 | <0.001 | <0.002 | 0.0082 | 0.07 | N/S | <0.02 | 0.0071 | N/S | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | N/S | 101.09 | 36.86 | 404 | N/S | N/S | N/S
2011-01-04 | 2.79 | 7.1 | 8.7 | 8 | 3 | N/S | <8 | <8 | 1565 | 224 | 2.78 | 0.98 | 14.38 | 1.51 | N/S | N/S | N/S | N/S | <0.04 | 0.0469 | <0.001 | <0.002 | 0.0074 | 0.08 | 0.01 | <0.02 | 0.0081 | <0.2 | <0.003 | <0.005 | <0.003 | 0.046 | <0.03 | <0.002 | <0.1 | <6 | 109.14 | 37.21 | 426 | T/X | <2.5 | 4.6
2011-01-05 | 2.06 | 7.5 | 8.1 | 8 | 5 | N/S | <8 | <8 | 1434 | 198 | 2.16 | <0.25 | 17.53 | 1.78 | N/S | N/S | N/S | N/S | <0.04 | 0.0443 | <0.001 | 0.0016 | 0.0082 | 0.13 | N/S | <0.02 | 0.0063 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 116.26 | 38.58 | 449 | N/S | N/S | N/S
2011-01-06 | 2.1 | 7.2 | 6.7 | 12 | 6 | N/S | 12 | 8 | 1466 | 170 | 2.57 | <0.25 | 19.22 | 2.15 | N/S | N/S | N/S | N/S | <0.04 | 0.054 | <0.001 | 0.0018 | 0.0105 | 0.13 | N/S | <0.02 | 0.0119 | N/S | <0.003 | <0.005 | <0.003 | 0.062 | <0.03 | <0.002 | <0.1 | N/S | 114.87 | 37.89 | 443 | N/S | N/S | N/S
2011-01-07 | 1.95 | 7.3 | 7.5 | N/S | N/S | N/S | <8 | <8 | 1276 | 164 | 2.1 | <0.25 | 19.71 | 2.05 | N/S | N/S | N/S | N/S | <0.04 | 0.0332 | <0.001 | <0.002 | 0.0143 | 0.07 | N/S | <0.02 | 0.0067 | N/S | <0.003 | <0.005 | <0.003 | 0.079 | <0.03 | <0.002 | <0.1 | N/S | 90.5 | 31.93 | 357 | N/S | N/S | N/S
2011-01-08 | 2.28 | 7.2 | 9 | N/S | N/S | N/S | 8 | <8 | 1227 | 154 | 3.07 | 1.1 | 20.42 | 2.07 | N/S | N/S | N/S | N/S | <0.04 | 0.0332 | <0.001 | <0.002 | 0.0119 | 0.09 | N/S | <0.02 | 0.0091 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 91.49 | 33.37 | 366 | N/S | N/S | N/S
2011-01-09 | 2.05 | 7.1 | 7.3 | 9 | 4 | N/S | 8 | <8 | 1299 | 154 | 2.5 | 0.46 | 19.63 | 2.04 | N/S | N/S | N/S | N/S | <0.04 | 0.0329 | <0.001 | <0.002 | 0.0093 | 0.08 | N/S | <0.02 | 0.0082 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 92.89 | 32.87 | 367 | N/S | N/S | N/S
2011-01-10 | 1.89 | 7.1 | 9 | 8 | 4 | 2.7 | <8 | <8 | 1315 | 166 | 1.59 | <0.25 | 19.22 | 1.88 | 0.005 | 11 | 0.98 | 35000 | <0.04 | 0.0322 | <0.001 | 0.0017 | 0.008 | 0.07 | N/S | <0.02 | 0.0085 | N/S | <0.003 | <0.005 | <0.003 | 0.056 | <0.03 | <0.002 | <0.1 | N/S | 89.89 | 33.56 | 363 | N/S | N/S | N/S
2011-01-11 | 1.91 | 7.1 | 9.3 | 8 | 4 | N/S | <8 | <8 | 1350 | 156 | 1.61 | <0.25 | 19.66 | 1.88 | N/S | N/S | N/S | N/S | <0.04 | 0.0302 | <0.001 | <0.002 | 0.0073 | 0.07 | N/S | <0.02 | 0.0074 | <0.2 | <0.003 | <0.005 | <0.003 | 0.046 | <0.03 | <0.002 | <0.1 | <6 | 85.04 | 32.45 | 346 | N/S | <2.5 | 4.9
2011-01-12 | 1.87 | 7.1 | 8.5 | 7 | 4 | N/S | <8 | <8 | 1556 | 160 | 1.99 | <0.25 | 20.46 | 1.94 | N/S | N/S | N/S | N/S | <0.04 | 0.0311 | <0.001 | <0.002 | 0.0124 | 0.07 | N/S | <0.02 | 0.0073 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 88.49 | 33.45 | 359 | N/S | N/S | N/S
2011-01-13 | 1.87 | 7.4 | 7.9 | 8 | 4 | N/S | <8 | <8 | 1723 | 216 | 1.43 | <0.25 | 21.78 | 2.02 | N/S | N/S | N/S | N/S | <0.04 | 0.0357 | <0.001 | 0.0015 | 0.0052 | 0.06 | N/S | <0.02 | 0.0059 | N/S | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | N/S | 103.72 | 34.13 | 400 | N/S | N/S | N/S
2011-01-14 | 1.89 | 7.6 | 8.6 | N/S | N/S | N/S | <8 | <8 | 1741 | 206 | 1.71 | <0.25 | 21.49 | 2.09 | N/S | N/S | N/S | N/S | <0.04 | 0.0378 | <0.001 | <0.002 | 0.005 | 0.07 | N/S | <0.02 | 0.0082 | N/S | <0.003 | <0.005 | <0.003 | 0.059 | <0.03 | <0.002 | <0.1 | N/S | 103.67 | 33.7 | 398 | N/S | N/S | N/S
2011-01-15 | 1.79 | 7.3 | 9.2 | N/S | N/S | N/S | <8 | <8 | 1681 | 178 | 1.9 | <0.25 | 21.31 | 2.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0366 | <0.001 | <0.002 | 0.0046 | 0.06 | N/S | <0.02 | 0.0095 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 94.66 | 32.41 | 370 | N/S | N/S | N/S
2011-01-16 | 1.89 | 7.3 | 8.5 | 8 | 3 | N/S | <8 | <8 | 1595 | 156 | 1.83 | <0.25 | 20.72 | 2.37 | N/S | N/S | N/S | N/S | <0.04 | 0.0319 | <0.001 | <0.002 | 0.0041 | 0.07 | N/S | <0.02 | 0.0075 | N/S | <0.003 | <0.005 | <0.003 | 0.054 | <0.03 | <0.002 | <0.1 | N/S | 83.66 | 30.07 | 333 | N/S | N/S | N/S
2011-01-17 | 2.06 | 7.3 | 8.5 | 9 | 5 | <2 | 8 | <8 | 1520 | 134 | 1.75 | <0.25 | 21.77 | 2.41 | <0.005 | 6 | 1.04 | N/S | <0.04 | 0.0317 | <0.001 | <0.002 | 0.007 | 0.07 | N/S | <0.02 | 0.0097 | N/S | <0.003 | <0.005 | <0.003 | 0.056 | <0.03 | <0.002 | <0.1 | N/S | 83 | 30.9 | 335 | N/S | N/S | N/S
2011-01-18 | 2.46 | 7.2 | 8.8 | 7 | 4 | N/S | 8 | <8 | 2259 | 180 | 1.83 | <0.25 | 17.34 | 2.03 | N/S | N/S | N/S | 3200 | <0.04 | 0.032 | <0.001 | <0.002 | 0.0064 | 0.07 | N/S | <0.02 | 0.009 | <0.2 | <0.003 | <0.005 | <0.003 | 0.058 | <0.03 | <0.002 | <0.1 | <6 | 82.27 | 29.51 | 327 | N/S | 2.5 | 3.5
2011-01-19 | 2.29 | 7.4 | 8.6 | 9 | 6 | N/S | 6 | <8 | 2263 | 212 | 1.84 | <0.25 | 18.83 | 2.3 | N/S | N/S | N/S | N/S | <0.04 | 0.0347 | <0.001 | <0.002 | 0.0094 | 0.08 | N/S | <0.02 | 0.0083 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 84.9 | 32.4 | 345 | N/S | N/S | N/S
2011-01-20 | 1.92 | 7.1 | 9.2 | 8 | 6 | N/S | 6 | <8 | 1851 | 208 | 1.55 | <0.25 | 21.7 | 2.48 | N/S | N/S | N/S | N/S | <0.04 | 0.0391 | <0.001 | <0.002 | 0.0116 | 0.08 | N/S | <0.02 | 0.0113 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 103.34 | 38.3 | 416 | N/S | N/S | N/S
2011-01-21 | 1.79 | 7.4 | 8.7 | N/S | N/S | N/S | 6 | <8 | 1591 | 188 | 1.45 | <0.25 | 21.87 | 2.57 | N/S | N/S | N/S | N/S | <0.04 | 0.0347 | <0.001 | 0.0018 | 0.0125 | 0.07 | N/S | <0.02 | 0.0065 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 94.2 | 35.69 | 382 | N/S | N/S | N/S
2011-01-22 | 1.88 | 7.2 | 9.5 | N/S | N/S | N/S | 11 | 8 | 1426 | 164 | 2.09 | 0.34 | 23.02 | 2.8 | N/S | N/S | N/S | N/S | <0.04 | 0.0336 | <0.001 | 0.0018 | 0.0183 | 0.09 | N/S | <0.02 | 0.0117 | N/S | <0.003 | <0.005 | <0.003 | 0.058 | <0.03 | <0.002 | <0.1 | N/S | 94.18 | 35.23 | 380 | N/S | N/S | N/S
2011-01-23 | 1.84 | 7.1 | 7 | 12 | 7 | N/S | 9 | 8 | 1287 | 218 | 2.67 | 0.31 | 22.33 | 2.87 | N/S | N/S | N/S | N/S | <0.04 | 0.0324 | <0.001 | 0.002 | 0.0196 | 0.1 | N/S | <0.02 | 0.0127 | N/S | <0.003 | <0.005 | <0.003 | 0.063 | <0.03 | <0.002 | <0.1 | N/S | 96.25 | 34.85 | 384 | N/S | N/S | N/S
2011-01-24 | 1.76 | 7.1 | 8.4 | 8 | 4 | 2 | <8 | <8 | 1229 | 130 | 1.97 | <0.25 | 21.76 | 2.59 | 0.006 | 6 | 1.06 | 3700 | <0.04 | 0.0284 | <0.001 | <0.002 | 0.0102 | 0.06 | N/S | <0.02 | 0.007 | N/S | <0.003 | <0.005 | <0.003 | 0.07 | <0.03 | <0.002 | <0.1 | N/S | 83.92 | 31.19 | 338 | N/S | N/S | N/S
2011-01-25 | 1.74 | 7.1 | 9.4 | 7 | 4 | N/S | <8 | <8 | 1250 | 136 | 1.85 | <0.25 | 20.25 | 2.43 | N/S | N/S | N/S | N/S | <0.04 | 0.0279 | <0.001 | <0.002 | 0.0092 | 0.07 | N/S | <0.02 | 0.006 | <0.2 | <0.003 | <0.005 | <0.003 | 0.053 | <0.03 | <0.002 | <0.1 | <6 | 85.64 | 30.96 | 341 | N/S | 9.1 | 5
2011-01-26 | 1.73 | 7.2 | 8.7 | 7 | 3 | N/S | <8 | <8 | 1196 | 142 | 1.76 | <0.25 | 21.14 | 2.52 | N/S | N/S | N/S | N/S | <0.04 | 0.0277 | <0.001 | <0.002 | 0.0107 | 0.08 | N/S | <0.02 | 0.0059 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 83.05 | 29.73 | 330 | N/S | N/S | N/S
2011-01-27 | 1.7 | 7.1 | 8.7 | 10 | 6 | N/S | <8 | <8 | 1331 | 194 | 1.7 | <0.25 | 21.57 | 2.48 | N/S | N/S | N/S | N/S | <0.04 | <0.02 | <0.001 | <0.002 | 0.0141 | 0.59 | N/S | <0.02 | 0.0659 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 112.01 | 35.1 | 424 | N/S | N/S | N/S
2011-01-28 | 1.7 | 7.3 | 8.2 | N/S | N/S | N/S | <8 | <8 | 1370 | 186 | 1.59 | <0.25 | 22.04 | 2.52 | N/S | N/S | N/S | N/S | <0.04 | <0.02 | <0.001 | <0.002 | <0.003 | <0.05 | N/S | <0.02 | 0.0015 | N/S | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | N/S | 96.81 | 32.24 | 375 | N/S | N/S | N/S
2011-01-29 | 1.85 | 7.2 | 9.1 | N/S | N/S | N/S | <8 | <8 | 1500 | 202 | 1.9 | 0.45 | 22.38 | 2.67 | N/S | N/S | N/S | N/S | <0.04 | 0.0394 | <0.001 | 0.0015 | 0.0059 | 0.05 | N/S | <0.02 | 0.0127 | N/S | <0.003 | <0.005 | <0.003 | 0.043 | <0.03 | <0.002 | <0.1 | N/S | 110.72 | 36.6 | 427 | N/S | N/S | N/S
2011-01-30 | 1.84 | 7.2 | 9.2 | 8 | 3 | N/S | <8 | <8 | 1514 | 200 | 1.77 | 0.47 | 22.15 | 2.71 | N/S | N/S | N/S | N/S | <0.04 | 0.0181 | <0.001 | <0.002 | <0.003 | <0.05 | N/S | <0.02 | 0.0015 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 105.54 | 35.16 | 408 | N/S | N/S | N/S
2011-01-31 | 1.76 | 7.2 | 8.8 | 8 | 5 | 2 | <8 | <8 | 1490 | 192 | 1.62 | <0.25 | 23.14 | 2.82 | 0.005 | 9 | 1.07 | 4400 | <0.04 | 0.0333 | <0.001 | <0.002 | 0.0235 | 0.05 | N/S | <0.02 | 0.0073 | N/S | 0.0049 | <0.005 | <0.003 | 0.061 | <0.03 | <0.002 | <0.1 | N/S | 99.09 | 34.52 | 390 | N/S | N/S | N/S
2011-02-01 | 1.69 | 7.2 | 8.6 | 7 | 3 | N/S | 8 | <8 | 1453 | 196 | 1.55 | <0.25 | 24.14 | 2.75 | N/S | N/S | N/S | N/S | <0.04 | 0.0311 | <0.001 | <0.002 | 0.0143 | 0.05 | <0.01 | <0.02 | 0.0059 | <0.2 | 0.003 | <0.005 | <0.003 | 0.11 | <0.03 | <0.002 | <0.1 | <6 | 91.23 | 33.35 | 365 | T/X | <2.5 | 4.5
2011-02-02 | 1.71 | 7.2 | 9.5 | 7 | 4 | N/S | <8 | <8 | 1426 | 174 | 1.57 | <0.25 | 24.9 | 2.72 | N/S | N/S | N/S | N/S | <0.04 | 0.0295 | <0.001 | <0.002 | 0.0144 | 0.05 | N/S | <0.02 | 0.0122 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 88.7 | 33.22 | 358 | N/S | N/S | N/S
2011-02-03 | 1.72 | 7.4 | 9 | 7 | 5 | N/S | <8 | <8 | 1375 | 172 | 1.52 | <0.25 | 24.56 | 2.68 | N/S | N/S | N/S | N/S | <0.04 | 0.0281 | <0.001 | <0.002 | 0.0063 | 0.07 | N/S | <0.02 | 0.0085 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 88.28 | 32.21 | 353 | N/S | N/S | N/S
2011-02-04 | 1.65 | 7.3 | 8.6 | N/S | N/S | N/S | <8 | <8 | 1350 | 166 | 1.45 | <0.25 | 24.14 | 2.78 | N/S | N/S | N/S | N/S | <0.04 | 0.0293 | <0.001 | 0.0015 | 0.0077 | 0.06 | N/S | <0.02 | 0.0074 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 97.33 | 34.6 | 386 | N/S | N/S | N/S
2011-02-05 | 1.8 | 7.1 | 8.7 | N/S | N/S | N/S | <8 | <8 | 1294 | 154 | 1.33 | <0.25 | 24.57 | 2.82 | N/S | N/S | N/S | N/S | <0.04 | 0.0279 | <0.001 | <0.002 | 0.0067 | 0.05 | N/S | <0.02 | 0.0083 | N/S | <0.003 | <0.005 | <0.003 | 0.043 | <0.03 | <0.002 | <0.1 | N/S | 90 | 32.66 | 359 | N/S | N/S | N/S
2011-02-06 | 1.79 | 7.1 | 9 | 7 | 4 | N/S | <8 | <8 | 1227 | 134 | 1.14 | 0.45 | 23.58 | 2.8 | N/S | N/S | N/S | N/S | <0.04 | 0.0264 | <0.001 | 0.0018 | 0.0078 | 0.08 | N/S | <0.02 | 0.0104 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 86.42 | 31.08 | 344 | N/S | N/S | N/S
2011-02-07 | 1.7 | 7.1 | 8.8 | 6 | 3 | <2 | <8 | <8 | 1334 | 164 | 1.44 | <0.25 | 24.24 | 2.82 | <0.005 | <6 | 1.09 | 3600 | <0.04 | 0.0279 | <0.001 | 0.0015 | 0.0066 | 0.05 | N/S | <0.02 | 0.0079 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 89.9 | 31.66 | 355 | N/S | N/S | N/S
2011-02-08 | 1.67 | 7.2 | 9 | 4 | 3 | N/S | <8 | <8 | 1338 | 140 | 1.4 | <0.25 | 25.18 | 2.9 | N/S | N/S | N/S | N/S | <0.04 | 0.0253 | <0.001 | <0.002 | 0.0056 | 0.05 | N/S | <0.02 | 0.0048 | <0.2 | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | <6 | 83.32 | 29.76 | 331 | N/S | 3.2 | 5
2011-02-09 | 1.69 | 7.2 | 10.3 | 5 | 3 | N/S | <8 | <8 | 1264 | 132 | 1.36 | <0.25 | 24.47 | 2.9 | N/S | N/S | N/S | N/S | <0.04 | 0.0224 | <0.001 | <0.002 | 0.0054 | <0.05 | N/S | <0.02 | 0.0042 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 71.14 | 26.67 | 287 | N/S | N/S | N/S
2011-02-10 | 1.72 | 7.3 | 9 | 5 | 3 | N/S | <8 | <8 | 1363 | 166 | 1.59 | <0.25 | 24.06 | 2.8 | N/S | N/S | N/S | N/S | <0.04 | 0.0327 | <0.001 | 0.0017 | 0.0057 | 0.05 | N/S | <0.02 | 0.0048 | N/S | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 106.25 | 33.71 | 404 | N/S | N/S | N/S
2011-02-11 | 1.7 | 7.2 | 8.4 | N/S | N/S | N/S | <8 | <8 | 1321 | 204 | 1.41 | <0.25 | 24.17 | 2.88 | N/S | N/S | N/S | N/S | <0.04 | 0.0318 | <0.001 | <0.002 | 0.0067 | <0.05 | N/S | <0.02 | 0.0049 | N/S | 0.003 | <0.005 | <0.003 | 0.051 | <0.03 | <0.002 | <0.1 | N/S | 102.82 | 34.09 | 397 | N/S | N/S | N/S
2011-02-12 | 1.78 | 7.2 | 9.2 | N/S | N/S | N/S | <8 | <8 | 1370 | 162 | 1.89 | 0.44 | 23.57 | 2.85 | N/S | N/S | N/S | N/S | <0.04 | 0.0307 | <0.001 | <0.002 | 0.0057 | <0.05 | N/S | <0.02 | 0.0092 | N/S | <0.003 | <0.005 | <0.003 | 0.041 | <0.03 | <0.002 | <0.1 | N/S | 95.29 | 31.59 | 368 | N/S | N/S | N/S
2011-02-13 | 1.82 | 7.1 | 8.9 | 7 | 5 | N/S | <8 | <8 | 1466 | 188 | 2.32 | 0.88 | 21.18 | 2.85 | N/S | N/S | N/S | N/S | <0.04 | 0.0311 | <0.001 | <0.002 | 0.0062 | <0.05 | N/S | <0.02 | 0.0174 | N/S | 0.0027 | <0.005 | <0.003 | 0.055 | <0.03 | <0.002 | <0.1 | N/S | 95.97 | 31.69 | 370 | N/S | N/S | N/S
2011-02-14 | 2.55 | 7.1 | 8.6 | 7 | 4 | <2 | <8 | <8 | 2022 | 188 | 1.74 | <0.25 | 17.43 | 2.28 | 0.005 | 7 | 0.86 | 27000 | <0.04 | 0.0354 | <0.001 | 0.0017 | 0.0097 | 0.12 | N/S | <0.02 | 0.0099 | N/S | <0.003 | <0.005 | <0.003 | 0.043 | <0.03 | <0.002 | <0.1 | N/S | 102.59 | 33.85 | 396 | N/S | N/S | N/S
2011-02-15 | 3.15 | 7.1 | 8.9 | 7 | 4 | N/S | 8 | <8 | 2256 | 206 | 1.33 | <0.25 | 15.78 | 1.68 | N/S | N/S | N/S | N/S | <0.04 | 0.0443 | <0.001 | 0.0015 | 0.0082 | 0.06 | N/S | <0.02 | 0.0081 | <0.2 | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | <6 | 105.31 | 37.35 | 417 | N/S | N/S | 3.2
2011-02-16 | 2.84 | 7.1 | 8.1 | 8 | 5 | N/S | <8 | <8 | 2117 | 176 | 1.55 | <0.25 | 13.5 | 1.62 | N/S | N/S | N/S | N/S | <0.04 | 0.0415 | <0.001 | 0.002 | 0.0083 | 0.08 | N/S | <0.02 | 0.0074 | N/S | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | N/S | 100.37 | 35.85 | 398 | N/S | 1.5 | N/S
2011-02-17 | 4.26 | 7.1 | 9.3 | 7 | 5 | N/S | 8 | <8 | 1699 | 154 | 1.21 | <0.25 | 8.51 | 0.97 | N/S | N/S | N/S | N/S | <0.04 | 0.0369 | <0.001 | 0.0015 | 0.0055 | 0.06 | N/S | <0.02 | 0.005 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 82.81 | 29.76 | 329 | N/S | N/S | N/S
2011-02-18 | 4.16 | 7.1 | 9.4 | N/S | N/S | N/S | 8 | <8 | 1422 | 180 | 1.4 | <0.25 | 8.28 | 0.82 | N/S | N/S | N/S | N/S | <0.04 | 0.0357 | <0.001 | <0.002 | 0.0056 | 0.07 | N/S | <0.02 | 0.0065 | N/S | <0.003 | <0.005 | <0.003 | 0.024 | <0.03 | <0.002 | <0.1 | N/S | 77.52 | 29.07 | 313 | N/S | N/S | N/S
2011-02-19 | 4.15 | 7.1 | 9.7 | N/S | N/S | N/S | 6 | <8 | 1487 | 176 | 1.26 | <0.25 | 10.24 | 0.9 | N/S | N/S | N/S | N/S | <0.04 | 0.0392 | <0.001 | 0.0022 | 0.0048 | 0.1 | N/S | <0.02 | 0.0078 | N/S | <0.003 | <0.005 | <0.003 | 0.052 | <0.03 | <0.002 | <0.1 | N/S | 88.85 | 32.25 | 355 | N/S | N/S | N/S
2011-02-20 | 4.2 | 7 | 8.4 | 8 | 4 | N/S | 5 | <8 | 1376 | 156 | 1.45 | <0.25 | 9.49 | 1.01 | N/S | N/S | N/S | N/S | <0.04 | 0.0377 | <0.001 | 0.0021 | 0.0063 | 0.09 | N/S | <0.02 | 0.0099 | N/S | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | N/S | 88.22 | 31.78 | 351 | N/S | N/S | N/S
2011-02-21 | 4.15 | 7.1 | 9 | 7 | 4 | <2 | 8 | <8 | 1251 | 164 | 1.33 | <0.25 | 8.43 | 0.84 | 0.006 | 17 | 0.46 | N/S | <0.04 | 0.035 | <0.001 | 0.0019 | 0.006 | 0.11 | N/S | <0.02 | 0.0073 | N/S | <0.003 | <0.005 | <0.003 | 0.031 | <0.03 | <0.002 | <0.1 | N/S | 82.03 | 30.17 | 329 | N/S | N/S | N/S
2011-02-22 | 4.11 | 7.1 | 8.5 | T/X | T/X | N/S | 9 | <8 | 1242 | 154 | 1.45 | <0.25 | 9.98 | 0.94 | N/S | N/S | N/S | 23000 | <0.04 | 0.0349 | <0.001 | 0.0018 | 0.0066 | 0.08 | N/S | <0.02 | 0.0069 | <0.2 | <0.003 | <0.005 | <0.003 | 0.031 | <0.03 | <0.002 | <0.1 | <6 | 81.9 | 31.12 | 333 | N/S | 3.6 | 7.5
2011-02-23 | 4.09 | 7.1 | 9 | 5 | 2 | N/S | <8 | <8 | 1321 | 164 | 1.34 | <0.25 | 11.13 | 1.13 | N/S | N/S | N/S | N/S | <0.04 | 0.0394 | <0.001 | 0.0018 | 0.0065 | 0.06 | N/S | <0.02 | 0.0063 | N/S | <0.003 | <0.005 | <0.003 | 0.027 | <0.03 | <0.002 | <0.1 | N/S | 91.76 | 35.81 | 377 | N/S | N/S | N/S
2011-02-24 | 3.3 | 7.1 | 8.8 | 6 | 3 | N/S | <8 | <8 | 1516 | 190 | 1.22 | <0.25 | 13.19 | 1.41 | N/S | N/S | N/S | N/S | <0.04 | 0.0449 | <0.001 | 0.0018 | 0.0072 | <0.05 | N/S | <0.02 | 0.0055 | N/S | <0.003 | <0.005 | <0.003 | 0.051 | <0.03 | <0.002 | <0.1 | N/S | 108.57 | 38.83 | 431 | N/S | N/S | N/S
2011-02-25 | 3.01 | 7.1 | 8.7 | N/S | N/S | N/S | <8 | <8 | 1416 | 146 | 3.24 | <0.25 | 13.8 | 1.62 | N/S | N/S | N/S | N/S | <0.04 | 0.04 | <0.001 | <0.002 | 0.0048 | 0.05 | N/S | <0.02 | 0.0069 | N/S | <0.003 | <0.005 | <0.003 | 0.041 | <0.03 | <0.002 | <0.1 | N/S | 100.87 | 37.62 | 407 | N/S | N/S | N/S
2011-02-26 | 2.37 | 7.2 | 9.6 | N/S | N/S | N/S | <8 | <8 | 1591 | 184 | 2.79 | <0.25 | 14.61 | 1.62 | N/S | N/S | N/S | N/S | <0.04 | 0.0408 | <0.001 | 0.0015 | 0.0055 | <0.05 | N/S | <0.02 | 0.0068 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 106.37 | 39.86 | 430 | N/S | N/S | N/S
2011-02-27 | 2.66 | 7.2 | 9.5 | 8 | 5 | N/S | <8 | <8 | 1689 | 194 | 3.18 | <0.25 | 13.75 | 1.57 | N/S | N/S | N/S | N/S | <0.04 | 0.0431 | <0.001 | <0.002 | 0.0085 | 0.1 | N/S | <0.02 | 0.0126 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 111.74 | 40.64 | 446 | N/S | N/S | N/S
2011-02-28 | 4.17 | 7.1 | 9.6 | 9 | 6 | 2.5 | 10 | <8 | 1471 | 184 | 3.25 | <0.25 | 9.99 | 1 | 0.006 | 7 | 0.54 | 4000 | <0.04 | 0.0385 | <0.001 | 0.0015 | 0.0071 | 0.11 | N/S | <0.02 | 0.0121 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 84.36 | 32.57 | 345 | N/S | N/S | N/S
2011-03-01 | 4.2 | 7.1 | 9.7 | 9 | 6 | N/S | 8 | <8 | 1430 | 176 | 3.03 | <0.25 | 10.06 | 0.93 | N/S | N/S | N/S | N/S | <0.04 | 0.038 | <0.001 | <0.002 | 0.0074 | 0.08 | <0.01 | <0.02 | 0.0087 | <0.2 | <0.003 | <0.005 | <0.003 | 0.03 | <0.03 | <0.002 | <0.1 | <6 | 88.99 | 33.88 | 362 | T/X | <2.5 | 3.9
2011-03-02 | 4.12 | 7.1 | 9.6 | 8 | 5 | N/S | <8 | <8 | 1418 | 180 | 3.32 | <0.25 | 10.85 | 1.1 | N/S | N/S | N/S | N/S | <0.04 | 0.0406 | <0.001 | <0.002 | 0.0064 | 0.07 | N/S | <0.02 | 0.0131 | N/S | <0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 94.54 | 36.31 | 386 | N/S | N/S | N/S
2011-03-03 | 3.24 | 7.2 | 9.2 | 8 | 5 | N/S | <8 | <8 | 1347 | 174 | 2.93 | 0.31 | 12.3 | 1.34 | N/S | N/S | N/S | N/S | <0.04 | 0.0371 | <0.001 | <0.002 | 0.0068 | 0.07 | N/S | <0.02 | 0.0157 | N/S | <0.003 | <0.005 | <0.003 | 0.029 | <0.03 | <0.002 | <0.1 | N/S | 90.32 | 35.71 | 373 | N/S | N/S | N/S
2011-03-04 | 2.62 | 7.2 | 8.2 | N/S | N/S | N/S | <8 | <8 | 1313 | 172 | 3.11 | <0.25 | 12.59 | 1.5 | N/S | N/S | N/S | N/S | <0.04 | 0.0381 | <0.001 | <0.002 | 0.0064 | 0.08 | N/S | <0.02 | 0.0144 | N/S | <0.003 | <0.005 | <0.003 | 0.035 | <0.03 | <0.002 | <0.1 | N/S | 94.19 | 36.93 | 387 | N/S | N/S | N/S
2011-03-05 | 4.18 | 7.1 | 9.3 | N/S | N/S | N/S | 8 | <8 | 992 | 152 | 2.46 | <0.25 | 9 | 0.91 | N/S | N/S | N/S | N/S | <0.04 | 0.0294 | <0.001 | <0.002 | 0.0062 | 0.08 | N/S | <0.02 | 0.0075 | N/S | <0.003 | <0.005 | <0.003 | 0.023 | <0.03 | <0.002 | <0.1 | N/S | 73.91 | 28.58 | 302 | N/S | N/S | N/S
2011-03-06 | 4.19 | 7.1 | 9.3 | 8 | 5 | N/S | 8 | <8 | 1079 | 152 | 2.89 | <0.25 | 10.08 | 0.87 | N/S | N/S | N/S | N/S | <0.04 | 0.0336 | <0.001 | <0.002 | 0.0068 | 0.08 | N/S | <0.02 | 0.0081 | N/S | <0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 82.93 | 32.87 | 342 | N/S | N/S | N/S
2011-03-07 | 4.18 | 7.1 | 8.3 | 8 | 6 | 2.4 | 8 | <8 | 1162 | 150 | 2.59 | <0.25 | 11.65 | 0.98 | <0.005 | 13 | 0.64 | 10000 | <0.04 | 0.0364 | <0.001 | <0.002 | 0.0059 | 0.06 | N/S | <0.02 | 0.0092 | N/S | <0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 88.29 | 35.38 | 366 | N/S | N/S | N/S
2011-03-08 | 3.23 | 7.1 | 8.7 | 8 | 6 | N/S | <8 | <8 | 1149 | 154 | 2.81 | <0.25 | 11.7 | 1.18 | N/S | N/S | N/S | N/S | <0.04 | 0.0363 | <0.001 | <0.002 | 0.0068 | 0.08 | N/S | <0.02 | 0.0079 | <0.2 | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | <6 | 90.48 | 37.03 | 378 | N/S | 1 | 4.9
2011-03-09 | 3.38 | 7.1 | 8.6 | 8 | 5 | N/S | <8 | <8 | 1152 | 156 | 3.1 | <0.25 | 11.66 | 1.14 | N/S | N/S | N/S | N/S | <0.04 | 0.0332 | <0.001 | <0.002 | 0.0074 | 0.07 | N/S | <0.02 | 0.0071 | N/S | <0.003 | <0.005 | <0.003 | 0.032 | <0.03 | <0.002 | <0.1 | N/S | 84 | 34.39 | 351 | N/S | N/S | N/S
2011-03-10 | 4.25 | 7.3 | 8.6 | 6 | 4 | N/S | <8 | <8 | 1097 | 140 | 2.77 | <0.25 | 10.77 | 0.96 | N/S | N/S | N/S | N/S | <0.04 | 0.0323 | <0.001 | <0.002 | 0.006 | 0.06 | N/S | <0.02 | 0.0067 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 80.56 | 33.39 | 339 | N/S | N/S | N/S
2011-03-11 | 3.39 | 7.1 | 7.8 | N/S | N/S | N/S | <8 | <8 | 1203 | 182 | 3.08 | <0.25 | 11.48 | 1.1 | N/S | N/S | N/S | N/S | <0.04 | 0.0382 | <0.001 | <0.002 | 0.007 | 0.08 | N/S | <0.02 | 0.007 | N/S | <0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 96.95 | 38.08 | 399 | N/S | N/S | N/S
2011-03-12 | 3.07 | 7.2 | 9.3 | N/S | N/S | N/S | <8 | <8 | 1278 | 200 | 3.13 | <0.25 | 13.36 | 1.23 | N/S | N/S | N/S | N/S | <0.04 | 0.0406 | <0.001 | <0.002 | 0.0055 | 0.05 | N/S | <0.02 | 0.0075 | N/S | <0.003 | <0.005 | <0.003 | 0.027 | <0.03 | <0.002 | <0.1 | N/S | 105.42 | 39.61 | 426 | N/S | N/S | N/S
2011-03-13 | 2.91 | 7.1 | 8.5 | 8 | 5 | N/S | <8 | <8 | 1240 | 176 | 3.57 | <0.25 | 14.49 | 1.58 | N/S | N/S | N/S | N/S | <0.04 | 0.036 | <0.001 | <0.002 | 0.007 | 0.09 | N/S | <0.02 | 0.012 | N/S | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | N/S | 92.06 | 36.63 | 381 | N/S | N/S | N/S
2011-03-14 | 2.82 | 7.1 | 8.8 | 8 | 5 | <2 | <8 | <8 | 1240 | 172 | 3.81 | <0.25 | 15.67 | 1.78 | 0.005 | 12 | 0.85 | 21000 | <0.04 | 0.0349 | <0.001 | <0.002 | 0.007 | 0.08 | N/S | <0.02 | 0.013 | N/S | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | N/S | 94.59 | 37.7 | 391 | N/S | N/S | N/S
2011-03-15 | 2.35 | 7.2 | 8.9 | 7 | 3 | N/S | <8 | <8 | 1239 | 168 | 3.64 | 0.26 | 17.2 | 1.96 | N/S | N/S | N/S | N/S | <0.04 | 0.0365 | <0.001 | 0.0018 | 0.0087 | 0.06 | N/S | <0.02 | 0.0114 | <0.2 | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | <6 | 101.9 | 40.01 | 419 | N/S | <0.5 | 4.9
2011-03-16 | 2.24 | 7.4 | 8.9 | 8 | 4 | N/S | <8 | <8 | 1291 | 180 | 3.17 | <0.25 | 18.05 | 2.11 | N/S | N/S | N/S | N/S | <0.04 | 0.0377 | <0.001 | <0.002 | 0.01 | 0.08 | N/S | <0.02 | 0.0114 | N/S | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 106.04 | 41.31 | 435 | N/S | N/S | N/S
2011-03-17 | 2.13 | 7.4 | 8.2 | 6 | 4 | N/S | 9 | <8 | 1302 | 202 | 3.21 | <0.25 | 17.96 | 2.13 | N/S | N/S | N/S | N/S | <0.04 | 0.0385 | <0.001 | 0.0016 | 0.0109 | 0.09 | N/S | <0.02 | 0.0099 | N/S | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | N/S | 107.41 | 41.58 | 439 | N/S | N/S | N/S
2011-03-18 | 2.21 | 7.4 | 7.8 | N/S | N/S | N/S | <8 | <8 | 1291 | 204 | 3.02 | <0.25 | 18.26 | 2.14 | N/S | N/S | N/S | N/S | <0.04 | 0.0349 | <0.001 | 0.0016 | 0.0065 | 0.08 | N/S | <0.02 | 0.0063 | N/S | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | N/S | 97.52 | 38.47 | 402 | N/S | N/S | N/S
2011-03-19 | 2.09 | 7.3 | 10 | N/S | N/S | N/S | <8 | <8 | 1295 | 182 | 3.68 | 0.48 | 17.97 | 2.24 | N/S | N/S | N/S | N/S | <0.04 | 0.0331 | <0.001 | <0.002 | 0.0074 | 0.12 | N/S | <0.02 | 0.0113 | N/S | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | N/S | 93.31 | 37.47 | 387 | N/S | N/S | N/S
2011-03-20 | 1.93 | 7.5 | 8 | 8 | 6 | N/S | <8 | <8 | 1221 | 180 | 3.92 | 0.34 | 16.86 | 2.22 | N/S | N/S | N/S | N/S | <0.04 | 0.0314 | <0.001 | <0.002 | 0.0067 | 0.08 | N/S | <0.02 | 0.0102 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 89.32 | 35.83 | 371 | N/S | N/S | N/S
2011-03-21 | 2.3 | 7.1 | 9.2 | 6 | 4 | 2 | <8 | <8 | 1149 | 168 | 3.22 | <0.25 | 16.23 | 2.14 | <0.005 | 11 | 0.81 | 22000 | <0.04 | 0.0269 | <0.001 | <0.002 | 0.0077 | 0.07 | N/S | <0.02 | 0.007 | N/S | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | N/S | 79.2 | 32.65 | 332 | N/S | N/S | N/S
2011-03-22 | 3.81 | 7.2 | 8.9 | 8 | 6 | N/S | 8 | 8 | 1071 | 164 | 3.13 | <0.25 | 13.32 | 1.61 | N/S | N/S | N/S | N/S | <0.04 | 0.0273 | <0.001 | <0.002 | 0.0082 | 0.11 | N/S | <0.02 | 0.008 | <0.2 | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | <6 | 78.46 | 30.84 | 323 | N/S | 1.8 | 5
2011-03-23 | 4.13 | 7.1 | 8.3 | 5 | 3 | N/S | <8 | <8 | 1075 | 170 | 2.53 | <0.25 | 10.13 | 1.09 | N/S | N/S | N/S | N/S | <0.04 | 0.0304 | <0.001 | <0.002 | 0.007 | 0.14 | N/S | <0.02 | 0.007 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 86.21 | 34.38 | 357 | N/S | N/S | N/S
2011-03-24 | 3.4 | 7 | 9.1 | 6 | 4 | N/S | <8 | <8 | 1074 | 138 | 2.35 | <0.25 | 11.21 | 1.1 | N/S | N/S | N/S | N/S | <0.04 | 0.0297 | <0.001 | <0.002 | 0.0064 | 0.07 | N/S | <0.02 | 0.0044 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 83.65 | 34.44 | 351 | N/S | N/S | N/S
2011-03-25 | 2.84 | 7.2 | 8.4 | N/S | N/S | N/S | <8 | <8 | 1104 | 168 | 2.4 | <0.25 | 13.24 | 1.44 | N/S | N/S | N/S | N/S | <0.04 | 0.0313 | <0.001 | <0.002 | 0.0106 | 0.05 | N/S | <0.02 | 0.0057 | N/S | <0.003 | <0.005 | <0.003 | 0.023 | <0.03 | <0.002 | <0.1 | N/S | 82.3 | 34.29 | 347 | N/S | N/S | N/S
2011-03-26 | 2.9 | 7.2 | 10.6 | N/S | N/S | N/S | <8 | <8 | 1058 | 138 | 2.41 | <0.25 | 14.62 | 1.68 | N/S | N/S | N/S | N/S | <0.04 | 0.03 | <0.001 | 0.0016 | 0.0089 | 0.05 | N/S | <0.02 | 0.0066 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 82.24 | 34.8 | 349 | N/S | N/S | N/S
2011-03-27 | 2.92 | 7.1 | 9.5 | 8 | 6 | N/S | <8 | <8 | 1099 | 168 | 3.37 | <0.25 | 15.13 | 1.95 | N/S | N/S | N/S | N/S | <0.04 | 0.0333 | <0.001 | 0.0016 | 0.0093 | 0.07 | N/S | <0.02 | 0.0116 | N/S | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 91.51 | 37.3 | 382 | N/S | N/S | N/S
2011-03-28 | 2.27 | 7.1 | 9.3 | 6 | 4 | 2 | <8 | <8 | 1135 | 178 | 2.84 | <0.25 | 15.92 | 2.01 | 0.005 | <6 | 0.8 | 6800 | <0.04 | 0.0314 | <0.001 | 0.0017 | 0.0083 | 0.06 | N/S | <0.02 | 0.0059 | N/S | <0.003 | <0.005 | <0.003 | 0.027 | <0.03 | <0.002 | <0.1 | N/S | 91.35 | 37.13 | 381 | N/S | N/S | N/S
2011-03-29 | 2.04 | 7.1 | 9.3 | 6 | 3 | N/S | <8 | <8 | 1093 | 134 | 3.63 | <0.25 | 17.46 | 2.2 | N/S | N/S | N/S | N/S | <0.04 | 0.0285 | <0.001 | <0.002 | 0.0078 | 0.05 | N/S | <0.02 | 0.0048 | <0.2 | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | <6 | 82.55 | 35.33 | 352 | N/S | <0.5 | 5.5
2011-03-30 | 2.23 | 7.2 | 8.9 | 7 | 5 | N/S | <8 | <8 | 1082 | 152 | 3.45 | <0.25 | 17.55 | 2.34 | N/S | N/S | N/S | N/S | <0.04 | 0.0306 | <0.001 | <0.002 | 0.0083 | 0.05 | N/S | <0.02 | 0.0058 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 87.46 | 36.74 | 370 | N/S | N/S | N/S
2011-03-31 | 1.99 | 7.3 | 8.3 | 6 | 5 | N/S | <8 | <8 | 1310 | 248 | 3.39 | <0.25 | 18.42 | 2.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0412 | <0.001 | 0.0016 | 0.0077 | 0.06 | N/S | <0.02 | 0.0054 | N/S | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | N/S | 119.58 | 41.95 | 471 | N/S | N/S | N/S
2011-04-01 | 2.09 | 7.3 | 8.3 | N/S | N/S | N/S | <8 | <8 | 1111 | 162 | 3 | <0.25 | 18.93 | 2.25 | N/S | N/S | N/S | N/S | <0.04 | 0.035 | <0.001 | 0.0015 | 0.0096 | 0.07 | N/S | <0.02 | 0.0068 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 100.88 | 38.44 | 410 | N/S | N/S | N/S
2011-04-02 | 2.25 | 7.2 | 8.3 | N/S | N/S | N/S | <8 | <8 | 1315 | 196 | 3.42 | <0.25 | 17.47 | 2.03 | N/S | N/S | N/S | N/S | <0.04 | 0.0392 | <0.001 | 0.0018 | 0.0084 | 0.06 | N/S | <0.02 | 0.0097 | N/S | <0.003 | <0.005 | 0.0001 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 108.26 | 39.5 | 433 | N/S | N/S | N/S
2011-04-03 | 2.21 | 7.1 | 8.2 | 6 | 6 | N/S | <8 | <8 | 1466 | 200 | 1.98 | 0.3 | 16.49 | 0.96 | N/S | N/S | N/S | N/S | <0.04 | 0.0419 | <0.001 | 0.0018 | 0.0096 | 0.16 | N/S | <0.02 | 0.0265 | N/S | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | N/S | 110.61 | 39.58 | 439 | N/S | N/S | N/S
2011-04-04 | 2.21 | 7.1 | 9.4 | 7 | 5 | 2.7 | <8 | <8 | 1431 | 200 | 3.69 | <0.25 | 16 | 1.83 | <0.005 | <6 | 0.83 | 11000 | <0.04 | 0.0354 | <0.001 | 0.0015 | 0.0085 | 0.08 | N/S | <0.02 | 0.0084 | N/S | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 94.55 | 34.93 | 380 | N/S | N/S | N/S
2011-04-05 | 2.35 | 7.2 | 8.8 | 7 | 5 | N/S | <8 | <8 | 1456 | 188 | 3.57 | <0.25 | 17.11 | 1.72 | N/S | N/S | N/S | N/S | <0.04 | 0.0378 | <0.001 | 0.0015 | 0.0075 | 0.08 | 0.029 | <0.02 | 0.006 | <0.2 | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | <6 | 100.29 | 37.85 | 406 | T/X | <0.5 | 6.3
2011-04-06 | 2.56 | 7.1 | 8.6 | 9 | 8 | N/S | <8 | <8 | 1560 | 204 | 3.69 | 0.27 | 17.43 | 1.93 | N/S | N/S | N/S | N/S | <0.04 | 0.0363 | <0.001 | 0.0015 | 0.0079 | 0.06 | N/S | <0.02 | 0.0134 | N/S | <0.003 | <0.005 | <0.003 | 0.03 | <0.03 | <0.002 | <0.1 | N/S | 96.58 | 36.29 | 391 | N/S | N/S | N/S
2011-04-07 | 2.06 | 7.3 | 8.3 | 6 | 3 | N/S | 8 | <8 | 1586 | 194 | 2.94 | <0.25 | 18.88 | 2.18 | N/S | N/S | N/S | N/S | <0.04 | 0.035 | <0.001 | 0.0017 | 0.007 | 0.12 | N/S | <0.02 | 0.0093 | N/S | <0.003 | <0.005 | <0.003 | 0.029 | <0.03 | <0.002 | <0.1 | N/S | 96.14 | 36.2 | 389 | N/S | N/S | N/S
2011-04-08 | 3.75 | 7.1 | 10.1 | N/S | N/S | N/S | <8 | <8 | 1063 | 142 | 2.9 | <0.25 | 13.16 | 1.47 | N/S | N/S | N/S | N/S | <0.04 | 0.0248 | <0.001 | 0.0015 | 0.0049 | 0.05 | N/S | <0.02 | 0.0035 | N/S | <0.003 | <0.005 | <0.003 | 0.024 | <0.03 | <0.002 | <0.1 | N/S | 70.26 | 27.35 | 288 | N/S | N/S | N/S
2011-04-09 | 4.24 | 7.1 | 9.2 | N/S | N/S | N/S | <8 | <8 | 1127 | 142 | 3.45 | <0.25 | 10.96 | 1.14 | N/S | N/S | N/S | N/S | <0.04 | 0.0283 | <0.001 | <0.002 | 0.0054 | 0.06 | N/S | <0.02 | 0.0056 | N/S | <0.003 | <0.005 | <0.003 | 0.02 | <0.03 | <0.002 | <0.1 | N/S | 76.59 | 30.76 | 318 | N/S | N/S | N/S
2011-04-10 | 2.82 | 7.1 | 9.7 | 8 | 5 | N/S | <8 | <8 | 1140 | 150 | 3.29 | <0.25 | 12.67 | 1.32 | N/S | N/S | N/S | N/S | <0.04 | 0.031 | <0.001 | 0.0018 | 0.0064 | 0.08 | N/S | <0.02 | 0.0056 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 83.03 | 34.81 | 351 | N/S | N/S | N/S
2011-04-11 | 2.93 | 7.1 | 8.4 | 5 | 5 | <2 | <8 | <8 | 1208 | 190 | 3.25 | <0.25 | 14.64 | 1.52 | <0.005 | 6 | 0.68 | N/S | <0.04 | 0.0303 | <0.001 | <0.002 | 0.0082 | 0.05 | N/S | <0.02 | 0.0055 | N/S | 0.0026 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 82.95 | 34.82 | 351 | N/S | N/S | N/S
2011-04-12 | 2.97 | 7.1 | 9.3 | 8 | 6 | N/S | 9 | <8 | 1089 | 160 | 3.46 | <0.25 | 16.67 | 1.81 | N/S | N/S | N/S | 21000 | <0.04 | 0.0287 | <0.001 | <0.002 | 0.0081 | 0.09 | N/S | <0.02 | 0.0094 | <0.2 | 0.0027 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | <6 | 78.42 | 33.41 | 333 | N/S | 2.3 | 5.8
2011-04-13 | 2.42 | 7.1 | 7.9 | 9 | 6 | N/S | 8 | <8 | 1099 | 186 | 3.59 | 0.29 | 17.18 | 2.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0303 | <0.001 | <0.002 | 0.0086 | 0.08 | N/S | <0.02 | 0.0117 | N/S | <0.003 | <0.005 | <0.003 | 0.03 | <0.03 | <0.002 | <0.1 | N/S | 86.11 | 36.75 | 366 | N/S | N/S | N/S
2011-04-14 | 2.05 | 7.1 | 7.8 | 7 | 4 | N/S | <8 | <8 | 1192 | 188 | 3.51 | <0.25 | 18.99 | 2.35 | N/S | N/S | N/S | N/S | <0.04 | 0.0344 | <0.001 | <0.002 | 0.0093 | 0.07 | N/S | <0.02 | 0.0093 | N/S | <0.003 | <0.005 | <0.003 | 0.035 | <0.03 | <0.002 | <0.1 | N/S | 102.22 | 42.17 | 429 | N/S | N/S | N/S
2011-04-15 | 2.1 | 7.1 | 10 | N/S | N/S | N/S | 10 | <8 | 1146 | 206 | 3.43 | <0.25 | 19.68 | 2.41 | N/S | N/S | N/S | N/S | <0.04 | 0.0312 | <0.001 | <0.002 | 0.01 | 0.12 | N/S | <0.02 | 0.0145 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 93.59 | 38.6 | 393 | N/S | N/S | N/S
2011-04-16 | 2.68 | 7.1 | 8 | N/S | N/S | N/S | <8 | <8 | 992 | 166 | 2.85 | <0.25 | 16.72 | 1.91 | N/S | N/S | N/S | N/S | <0.04 | 0.0283 | <0.001 | <0.002 | 0.0097 | 0.09 | N/S | <0.02 | 0.0068 | N/S | <0.003 | <0.005 | <0.003 | 0.032 | <0.03 | <0.002 | <0.1 | N/S | 82.9 | 35.58 | 354 | N/S | N/S | N/S
2011-04-17 | 2.62 | 7.1 | 9.1 | 9 | 5 | N/S | 10 | 9 | 1020 | 160 | 3.11 | <0.25 | 16.35 | 1.86 | N/S | N/S | N/S | N/S | <0.04 | 0.0281 | <0.001 | 0.0015 | 0.0123 | 0.13 | N/S | <0.02 | 0.0108 | N/S | 0.0028 | <0.005 | <0.003 | 0.035 | <0.03 | <0.002 | <0.1 | N/S | 79.26 | 33.15 | 334 | N/S | N/S | N/S
2011-04-18 | 2.95 | 7.1 | 8 | 8 | 5 | 2.7 | 8 | <8 | 936 | 132 | 2.87 | <0.25 | 14.09 | 1.57 | 0.005 | <6 | 0.63 | 4400 | <0.04 | 0.0252 | <0.001 | <0.002 | 0.0124 | 0.09 | N/S | <0.02 | 0.0062 | N/S | <0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 70.71 | 28.92 | 296 | N/S | N/S | N/S
2011-04-19 | 3.81 | 7.1 | 9.4 | 9 | 4 | N/S | 10 | 8 | 888 | 126 | 2.86 | <0.25 | 12.72 | 1.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0268 | <0.001 | 0.0016 | 0.0125 | 0.2 | N/S | <0.02 | 0.0082 | <0.2 | <0.003 | <0.005 | <0.003 | 0.027 | <0.03 | <0.002 | <0.1 | <6 | 71.8 | 30.12 | 303 | N/S | 3.3 | 5.9
2011-04-20 | 4.29 | 7.1 | 8.5 | 10 | 5 | N/S | <8 | <8 | 816 | 122 | 3.06 | <0.25 | 9.35 | 0.9 | N/S | N/S | N/S | N/S | <0.04 | 0.0248 | <0.001 | 0.0019 | 0.0086 | 0.11 | N/S | <0.02 | 0.0054 | N/S | <0.003 | <0.005 | <0.003 | 0.023 | <0.03 | <0.002 | <0.1 | N/S | 66.44 | 28.2 | 282 | N/S | N/S | N/S
2011-04-21 | 4.22 | 7.2 | 8.8 | 8 | 5 | N/S | 8 | <8 | 884 | 144 | 2.53 | <0.25 | 10.95 | 0.94 | N/S | N/S | N/S | N/S | <0.04 | 0.0271 | <0.001 | 0.0022 | 0.0103 | 0.11 | N/S | <0.02 | 0.007 | N/S | 0.0026 | <0.005 | <0.003 | 0.035 | <0.03 | <0.002 | <0.1 | N/S | 69.75 | 30.37 | 299 | N/S | N/S | N/S
2011-04-22 | 4.21 | 7.1 | 8.3 | N/S | N/S | N/S | <8 | <8 | 672 | 138 | 2.57 | <0.25 | 9.02 | 0.98 | N/S | N/S | N/S | N/S | <0.04 | 0.024 | <0.001 | 0.0017 | 0.0081 | 0.07 | N/S | <0.02 | 0.0052 | N/S | <0.003 | <0.005 | <0.003 | 0.024 | <0.03 | <0.002 | <0.1 | N/S | 62.59 | 27.21 | 268 | N/S | N/S | N/S
2011-04-23 | 4.22 | 7 | 9.5 | N/S | N/S | N/S | <8 | <8 | 666 | 102 | 2.42 | <0.25 | 7.75 | 0.78 | N/S | N/S | N/S | N/S | <0.04 | 0.0224 | <0.001 | <0.002 | 0.0073 | 0.09 | N/S | <0.02 | 0.0048 | N/S | <0.003 | <0.005 | <0.003 | 0.022 | <0.03 | <0.002 | <0.1 | N/S | 57.6 | 24.98 | 247 | N/S | N/S | N/S
2011-04-24 | 4.19 | 7.1 | 8.6 | 9 | 5 | N/S | 8 | <8 | 864 | 142 | 2.66 | <0.25 | 10.38 | 0.99 | N/S | N/S | N/S | N/S | <0.04 | 0.0291 | <0.001 | 0.0015 | 0.0086 | 0.11 | N/S | <0.02 | 0.0076 | N/S | 0.0025 | <0.005 | <0.003 | 0.027 | <0.03 | <0.002 | <0.1 | N/S | 73.05 | 30.93 | 310 | N/S | N/S | N/S
2011-04-25 | 4.17 | 7 | 4.3 | 11 | 5 | 2.6 | 11 | 8 | 860 | 128 | 3.23 | 0.53 | 12.38 | 1.48 | <0.005 | 8 | 0.57 | 3200 | <0.04 | 0.0285 | <0.001 | 0.0015 | 0.01 | 0.1 | N/S | <0.02 | 0.0117 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 70.79 | 30.5 | 302 | N/S | N/S | N/S
2011-04-26 | 4.38 | 7 | 7.8 | 9 | 4 | N/S | <8 | <8 | 692 | 100 | 2.56 | <0.25 | 9.87 | 1.11 | N/S | N/S | N/S | N/S | <0.04 | 0.0254 | <0.001 | <0.002 | 0.01 | 0.13 | N/S | <0.02 | 0.0069 | <0.2 | 0.0041 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | <6 | 63.77 | 27.37 | 272 | N/S | 4.1 | 5.5
2011-04-27 | 4.51 | 7.1 | 9.8 | 8 | 5 | N/S | 10 | 9 | 678 | 118 | 2.88 | <0.25 | 9.11 | 0.94 | N/S | N/S | N/S | N/S | <0.04 | 0.0257 | <0.001 | 0.0019 | 0.0084 | 0.12 | N/S | <0.02 | 0.0069 | N/S | 0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 64.91 | 28.48 | 279 | N/S | N/S | N/S
2011-04-28 | 4.5 | 7 | 7.8 | 9 | 5 | N/S | 9 | <8 | 714 | 132 | 2.57 | <0.25 | 9.6 | 0.93 | N/S | N/S | N/S | N/S | <0.04 | 0.0268 | <0.001 | 0.0025 | 0.0108 | 0.1 | N/S | <0.02 | 0.0062 | N/S | 0.0034 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 68.1 | 29.62 | 292 | N/S | N/S | N/S
2011-04-29 | 4.32 | 7 | 8.3 | N/S | N/S | N/S | <8 | <8 | 818 | 116 | 1.54 | <0.25 | 11.5 | 1.05 | N/S | N/S | N/S | N/S | <0.04 | 0.0301 | <0.001 | 0.0019 | 0.0085 | 0.09 | N/S | <0.02 | 0.0073 | N/S | 0.0033 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 74.12 | 32.81 | 320 | N/S | N/S | N/S
2011-04-30 | 3.63 | 7 | 8.2 | N/S | N/S | N/S | <8 | <8 | 862 | 122 | 1.98 | <0.25 | 12.12 | 1.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0322 | <0.001 | 0.0019 | 0.0094 | 0.1 | N/S | <0.02 | 0.012 | N/S | 0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 81.89 | 35.9 | 352 | N/S | N/S | N/S
2011-05-01 | 3.18 | 7 | 7.9 | 11 | 6 | N/S | 10 | <8 | 904 | 102 | 2.64 | 0.48 | 12.93 | 1.74 | N/S | N/S | N/S | N/S | <0.04 | 0.0317 | <0.001 | 0.0023 | 0.0105 | 0.13 | N/S | <0.02 | 0.0194 | N/S | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | N/S | 83.14 | 35.54 | 354 | N/S | N/S | N/S
2011-05-02 | 2.32 | 7.1 | 8 | 9 | 3 | 3.1 | <8 | <8 | 924 | 150 | 3.12 | <0.25 | 15.09 | 1.74 | 0.005 | <6 | 0.75 | 7500 | <0.04 | 0.0304 | <0.001 | 0.0023 | 0.0102 | 0.09 | N/S | <0.02 | 0.0114 | N/S | <0.003 | <0.005 | <0.003 | 0.061 | <0.03 | <0.002 | <0.1 | N/S | 84.79 | 35.9 | 360 | N/S | N/S | N/S
2011-05-03 | 2.28 | 7.1 | 8.4 | 8 | 4 | N/S | <8 | <8 | 936 | 140 | 3.23 | <0.25 | 17.26 | 1.8 | N/S | N/S | N/S | N/S | <0.04 | 0.0301 | <0.001 | 0.0025 | 0.0122 | 0.09 | 0.058 | <0.02 | 0.0092 | <0.2 | <0.003 | <0.005 | <0.003 | 0.053 | <0.03 | <0.002 | <0.1 | <6 | 83.86 | 35.9 | 357 | T/X | 7.6 | 6.4
2011-05-04 | 2.09 | 7.3 | 8.2 | 7 | 4 | N/S | <8 | <8 | 972 | 176 | 3.68 | <0.25 | 18.31 | 2.07 | N/S | N/S | N/S | N/S | <0.04 | 0.0297 | <0.001 | 0.0019 | 0.0116 | 0.1 | N/S | <0.02 | 0.01 | N/S | 0.0031 | <0.005 | <0.003 | 0.053 | <0.03 | <0.002 | <0.1 | N/S | 85.6 | 36.03 | 362 | N/S | N/S | N/S
2011-05-05 | 2.33 | 7.3 | 8.1 | 8 | 4 | N/S | 10 | 8 | 1210 | 232 | 4.35 | 0.41 | 18.33 | 2.18 | N/S | N/S | N/S | N/S | <0.04 | 0.0614 | <0.001 | 0.0046 | 0.0857 | 1.48 | N/S | <0.02 | 0.067 | N/S | 0.0054 | <0.005 | <0.003 | 0.134 | <0.03 | <0.002 | <0.1 | N/S | 113.22 | 39.92 | 447 | N/S | N/S | N/S
2011-05-06 | 2.47 | 7.1 | 8.9 | N/S | N/S | N/S | 9 | <8 | 1154 | 236 | 3.5 | 0.32 | 17.5 | 2.58 | N/S | N/S | N/S | N/S | <0.04 | 0.0355 | <0.001 | 0.0019 | 0.0123 | 0.1 | N/S | <0.02 | 0.0144 | N/S | 0.0032 | <0.005 | <0.003 | 0.051 | <0.03 | <0.002 | <0.1 | N/S | 104.53 | 39.03 | 422 | N/S | N/S | N/S
2011-05-07 | 2.25 | 7.1 | 8.4 | N/S | N/S | N/S | 8 | <8 | 1103 | 222 | 3.74 | 0.88 | 16.79 | 2.66 | N/S | N/S | N/S | N/S | <0.04 | 0.0335 | <0.001 | <0.002 | 0.0106 | 0.09 | N/S | <0.02 | 0.0182 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 98.09 | 38.68 | 404 | N/S | N/S | N/S
2011-05-08 | 2.09 | 7.1 | 7.9 | 9 | 4 | N/S | 8 | <8 | 1092 | 206 | 4.99 | 1.04 | 16.79 | 3.04 | N/S | N/S | N/S | N/S | <0.04 | 0.0342 | <0.001 | 0.0016 | 0.013 | 0.1 | N/S | <0.02 | 0.0188 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 101.16 | 39.45 | 415 | N/S | N/S | N/S
2011-05-09 | 2.02 | 7.1 | 7.7 | 9 | 6 | 2 | <8 | <8 | 1168 | 232 | 4.42 | 0.79 | 17.71 | 2.78 | <0.005 | 6 | 0.88 | 54000 | <0.04 | 0.0354 | <0.001 | 0.0017 | 0.0126 | 0.11 | N/S | <0.02 | 0.0161 | N/S | <0.003 | <0.005 | <0.003 | 0.062 | <0.03 | <0.002 | <0.1 | N/S | 103.46 | 40.69 | 426 | N/S | N/S | N/S
2011-05-10 | 2.02 | 7.1 | 8.2 | 8 | 4 | N/S | 10 | <8 | 1156 | 196 | 3.43 | 0.61 | 19.14 | 2.6 | N/S | N/S | N/S | N/S | <0.04 | 0.0342 | <0.001 | <0.002 | 0.0125 | 0.12 | N/S | <0.02 | 0.0172 | <0.2 | <0.003 | <0.005 | <0.003 | 0.064 | <0.03 | <0.002 | <0.1 | <6 | 99.88 | 39.64 | 413 | N/S | 3.3 | 6.2
2011-05-11 | 2.04 | 7.2 | 7 | 6 | 3 | N/S | 9 | <8 | 1358 | 232 | 4.49 | 0.37 | 19.48 | 2.68 | N/S | N/S | N/S | N/S | <0.04 | 0.0373 | <0.001 | <0.002 | 0.0146 | 0.14 | N/S | <0.02 | 0.0126 | N/S | 0.0034 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 105.23 | 41.45 | 433 | N/S | N/S | N/S
2011-05-12 | 2.06 | 7.2 | 6.9 | 6 | 3 | N/S | <8 | <8 | 1193 | 202 | 4.79 | 0.34 | 19.96 | 2.93 | N/S | N/S | N/S | N/S | <0.04 | 0.0345 | <0.001 | <0.002 | 0.0118 | 0.12 | N/S | <0.02 | 0.0136 | N/S | 0.0025 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 96.82 | 38.74 | 401 | N/S | N/S | N/S
2011-05-13 | 2.03 | 7 | 7.3 | N/S | N/S | N/S | 8 | <8 | 1069 | 160 | 4 | 0.29 | 20.12 | 3.01 | N/S | N/S | N/S | N/S | <0.04 | 0.0292 | <0.001 | <0.002 | 0.0108 | 0.11 | N/S | <0.02 | 0.0092 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 83.35 | 34.52 | 350 | N/S | N/S | N/S
2011-05-14 | 2.07 | 7.1 | 8.1 | N/S | N/S | N/S | 10 | <8 | 1102 | 166 | 4.26 | 0.4 | 19.43 | 2.88 | N/S | N/S | N/S | N/S | <0.04 | 0.0288 | <0.001 | <0.002 | 0.0123 | 0.11 | N/S | <0.02 | 0.0138 | N/S | 0.0101 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 87.67 | 35.16 | 364 | N/S | N/S | N/S
2011-05-15 | 2.64 | 7 | 7.3 | 14 | 7 | N/S | 14 | 12 | 942 | 142 | 4.36 | 0.25 | 17.03 | 2.44 | N/S | N/S | N/S | N/S | <0.04 | 0.0272 | <0.001 | <0.002 | 0.0128 | 0.1 | N/S | <0.02 | 0.0187 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 78.52 | 31.77 | 327 | N/S | N/S | N/S
2011-05-16 | 2.47 | 7 | 7.4 | 10 | 5 | 2.1 | 8 | <8 | 928 | 138 | 3.12 | <0.25 | 15.51 | 2.32 | <0.005 | 6 | 0.88 | 5600 | <0.04 | 0.027 | <0.001 | <0.002 | 0.0116 | 0.1 | N/S | <0.02 | 0.0217 | N/S | <0.003 | <0.005 | <0.003 | 0.049 | <0.03 | <0.002 | <0.1 | N/S | 77.22 | 31.28 | 322 | N/S | N/S | N/S
2011-05-17 | 1.98 | 7 | 9.5 | 10 | 7 | N/S | 6 | <8 | 954 | 154 | 2.31 | 0.39 | 16.34 | 2.52 | N/S | N/S | N/S | N/S | <0.04 | 0.0271 | <0.001 | <0.002 | 0.0096 | 0.08 | N/S | <0.02 | 0.0178 | <0.2 | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | <6 | 77.44 | 31.11 | 321 | N/S | 1.2 | 6.2
2011-05-18 | 1.89 | 7 | 8.5 | 11 | 7 | N/S | <8 | <8 | 1008 | 172 | 2.93 | 0.54 | 20.22 | 3.11 | N/S | N/S | N/S | N/S | <0.04 | 0.0294 | <0.001 | 0.0017 | 0.0117 | 0.09 | N/S | <0.02 | 0.017 | N/S | <0.003 | <0.005 | <0.003 | 0.063 | <0.03 | <0.002 | <0.1 | N/S | 84.04 | 33.4 | 347 | N/S | N/S | N/S
2011-05-19 | 1.93 | 7.1 | 6.9 | 13 | 8 | N/S | 13 | 8 | 1046 | 180 | 3.47 | 0.72 | 21.6 | 3.49 | N/S | N/S | N/S | N/S | <0.04 | 0.0293 | <0.001 | <0.002 | 0.0164 | 0.12 | N/S | <0.02 | 0.0126 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 83.43 | 33.84 | 348 | N/S | N/S | N/S
2011-05-20 | 1.81 | 7.5 | 6.7 | N/S | N/S | N/S | <8 | <8 | 1147 | 208 | 4.65 | 0.58 | 22.89 | 3.36 | N/S | N/S | N/S | N/S | <0.04 | 0.0302 | <0.001 | <0.002 | 0.0139 | 0.08 | N/S | <0.02 | 0.0112 | N/S | 0.0027 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 90.47 | 36.01 | 374 | N/S | N/S | N/S
2011-05-21 | 1.98 | 7.1 | 7 | N/S | N/S | N/S | <8 | <8 | 1093 | 192 | 4.38 | 1.07 | 20.19 | 3.23 | N/S | N/S | N/S | N/S | <0.04 | 0.0279 | <0.001 | 0.0016 | 0.0116 | 0.08 | N/S | <0.02 | 0.0102 | N/S | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 81.32 | 32.79 | 338 | N/S | N/S | N/S
2011-05-22 | 2.01 | 7.1 | 6.6 | 14 | 9 | N/S | 13 | 10 | 996 | 154 | 4.88 | 1.22 | 18.6 | 3.26 | N/S | N/S | N/S | N/S | <0.04 | 0.025 | <0.001 | 0.0018 | 0.0117 | 0.1 | N/S | <0.02 | 0.0122 | N/S | <0.003 | <0.005 | <0.003 | 0.048 | <0.03 | <0.002 | <0.1 | N/S | 70.68 | 28.75 | 295 | N/S | N/S | N/S
2011-05-23 | 1.94 | 7 | 6.2 | 8 | 5 | <2 | <8 | <8 | 916 | 98 | 3.06 | 0.82 | 18.6 | 3.09 | 0.005 | 6 | 1 | 45000 | <0.04 | 0.0259 | <0.001 | 0.0016 | 0.0086 | 0.07 | N/S | <0.02 | 0.009 | N/S | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | N/S | 74.11 | 30.15 | 309 | N/S | N/S | N/S
2011-05-24 | 1.88 | 7 | 7.4 | 7 | 5 | N/S | <8 | <8 | 1057 | 154 | 2.86 | 0.45 | 21.23 | 3.18 | N/S | N/S | N/S | N/S | <0.04 | 0.0293 | <0.001 | 0.0023 | 0.0089 | 0.12 | N/S | <0.02 | 0.0073 | <0.2 | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | <6 | 85.58 | 34.12 | 354 | N/S | 4 | 6.7
2011-05-25 | 3.21 | 7 | 6.9 | 8 | 7 | N/S | 14 | 11 | 934 | 178 | 3.86 | 0.91 | 16.69 | 2.34 | N/S | N/S | N/S | N/S | <0.04 | 0.0261 | <0.001 | 0.002 | 0.0087 | 0.13 | N/S | <0.02 | 0.0079 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 76.37 | 28.41 | 308 | N/S | N/S | N/S
2011-05-26 | 4.46 | 7 | 7.8 | 8 | 6 | N/S | 13 | 9 | 706 | 168 | 1.99 | <0.25 | 7.72 | 1.09 | N/S | N/S | N/S | N/S | <0.04 | 0.021 | <0.001 | 0.0018 | 0.0058 | 0.15 | N/S | <0.02 | 0.0062 | N/S | <0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 58.4 | 22.63 | 239 | N/S | N/S | N/S
2011-05-27 | 4.38 | 7 | 8.9 | N/S | N/S | N/S | 10 | <8 | 820 | 122 | 2.52 | <0.25 | 8.7 | 1.06 | N/S | N/S | N/S | N/S | <0.04 | 0.0269 | <0.001 | 0.0016 | 0.0054 | 0.25 | N/S | <0.02 | 0.008 | N/S | <0.003 | <0.005 | <0.003 | 0.024 | <0.03 | <0.002 | <0.1 | N/S | 72.22 | 28.18 | 296 | N/S | N/S | N/S
2011-05-28 | 4.24 | 7 | 7.1 | N/S | N/S | N/S | <8 | <8 | 918 | 142 | 2.45 | 0.28 | 9.9 | 1.28 | N/S | N/S | N/S | N/S | <0.04 | 0.0292 | <0.001 | 0.002 | 0.0055 | 0.09 | N/S | <0.02 | 0.008 | N/S | <0.003 | <0.005 | <0.003 | 0.032 | <0.03 | <0.002 | <0.1 | N/S | 78.14 | 30.22 | 320 | N/S | N/S | N/S
2011-05-29 | 3.65 | 6.9 | 7.5 | 7 | 5 | N/S | <8 | <8 | 836 | 116 | 2.17 | <0.25 | 10.41 | 1.44 | N/S | N/S | N/S | N/S | <0.04 | 0.0264 | <0.001 | 0.0016 | 0.0056 | 0.09 | N/S | <0.02 | 0.0051 | N/S | <0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 70.68 | 28.76 | 295 | N/S | N/S | N/S
2011-05-30 | 4.31 | 6.9 | 7.2 | 7 | 4 | <2 | 8 | <8 | 758 | 130 | 1.44 | <0.25 | 9.8 | 1.26 | <0.005 | <6 | 0.53 | N/S | <0.04 | 0.027 | <0.001 | 0.0019 | 0.0068 | 0.11 | N/S | <0.02 | 0.0054 | N/S | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | N/S | 71.2 | 28.95 | 297 | N/S | N/S | N/S
2011-05-31 | 4.29 | 6.9 | 7 | 7 | 4 | N/S | <8 | <8 | 786 | 118 | 2.14 | <0.25 | 10.53 | 1.28 | N/S | N/S | N/S | 4400 | <0.04 | 0.031 | <0.001 | 0.0018 | 0.0083 | 0.09 | N/S | <0.02 | 0.0068 | <0.2 | <0.003 | <0.005 | <0.003 | 0.036 | <0.03 | <0.002 | <0.1 | <6 | 81.96 | 32.71 | 339 | N/S | 1.7 | 5.6
2011-06-01 | 3.62 | 6.9 | 7.2 | 8 | 5 | N/S | <8 | <8 | 892 | 136 | 3.67 | 0.26 | 12.39 | 1.71 | N/S | N/S | N/S | N/S | <0.04 | 0.0286 | <0.001 | 0.0018 | 0.0096 | 0.11 | N/S | <0.02 | 0.0096 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 73.26 | 31.67 | 313 | N/S | N/S | N/S
2011-06-02 | 2.39 | 7 | 7 | 7 | 5 | N/S | <8 | <8 | 894 | 114 | 3.02 | 0.25 | 12.95 | 2.21 | N/S | N/S | N/S | N/S | <0.04 | 0.0295 | <0.001 | 0.0016 | 0.0079 | 0.08 | N/S | <0.02 | 0.0056 | N/S | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | N/S | 80.98 | 34.57 | 345 | N/S | N/S | N/S
2011-06-03 | 2.33 | 7.2 | 6.3 | N/S | N/S | N/S | <8 | <8 | 1144 | 230 | 3.06 | 0.32 | 17.24 | 2.49 | N/S | N/S | N/S | N/S | <0.04 | 0.039 | <0.001 | 0.0016 | 0.0086 | 0.09 | N/S | <0.02 | 0.0062 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 107.93 | 39.74 | 433 | N/S | N/S | N/S
2011-06-04 | 2.26 | 7.1 | 7.7 | N/S | N/S | N/S | 8 | <8 | 1360 | 318 | 3.66 | 0.35 | 16.31 | 2.56 | N/S | N/S | N/S | N/S | <0.04 | 0.0442 | <0.001 | 0.0023 | 0.0072 | 0.1 | N/S | <0.02 | 0.0059 | N/S | <0.003 | <0.005 | <0.003 | 0.055 | <0.03 | <0.002 | <0.1 | N/S | 125.35 | 43.23 | 491 | N/S | N/S | N/S
2011-06-05 | 2.57 | 7.1 | 7.1 | 6 | 4 | N/S | <8 | <8 | 1191 | 228 | 3.19 | 0.27 | 15.14 | 2.23 | N/S | N/S | N/S | N/S | <0.04 | 0.0366 | <0.001 | 0.0015 | 0.0069 | 0.07 | N/S | <0.02 | 0.0051 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 103.4 | 36.91 | 410 | N/S | N/S | N/S
2011-06-06 | 2.51 | 7 | 7.8 | 8 | 5 | 2 | 8 | <8 | 1343 | 338 | 3.93 | 0.28 | 16.71 | 2.32 | <0.005 | 7 | 0.78 | 9200 | <0.04 | 0.0362 | <0.001 | 0.0018 | 0.009 | 0.08 | N/S | <0.02 | 0.0082 | N/S | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 98.58 | 36.06 | 395 | N/S | N/S | N/S
2011-06-07 | 2.47 | 7 | 8.2 | 7 | 4 | N/S | <8 | <8 | 1394 | 298 | 4.3 | 0.26 | 15.4 | 2.52 | N/S | N/S | N/S | N/S | <0.04 | 0.0391 | <0.001 | <0.002 | 0.0088 | 0.06 | 0.072 | <0.02 | 0.0074 | <0.2 | <0.003 | <0.005 | <0.003 | 0.04 | <0.03 | <0.002 | <0.1 | <6 | 107.11 | 39.25 | 429 | T/X | <0.5 | 5.8
2011-06-08 | 2.39 | 7 | 7.6 | 11 | 5 | N/S | 12 | <8 | 1374 | 246 | 4.68 | 0.32 | 15.63 | 2.97 | N/S | N/S | N/S | N/S | <0.04 | 0.0353 | <0.001 | 0.0024 | 0.0121 | 0.11 | N/S | <0.02 | 0.0181 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 101.06 | 37.93 | 409 | N/S | N/S | N/S
2011-06-09 | 4.08 | 7 | 7 | 8 | 4 | N/S | 10 | <8 | 734 | 132 | 3.78 | <0.25 | 8.61 | 1.41 | N/S | N/S | N/S | N/S | <0.04 | 0.0231 | <0.001 | 0.002 | 0.0098 | 0.14 | N/S | <0.02 | 0.0061 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 63.34 | 23.59 | 255 | N/S | N/S | N/S
2011-06-10 | 4.51 | 7 | 8.3 | N/S | N/S | N/S | 13 | 12 | 746 | 148 | 4.93 | <0.25 | 7.4 | 1.1 | N/S | N/S | N/S | N/S | <0.04 | 0.0276 | <0.001 | 0.0017 | 0.0114 | 0.18 | N/S | <0.02 | 0.0366 | N/S | 0.0026 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | N/S | 68.04 | 26.89 | 281 | N/S | N/S | N/S
2011-06-11 | 4.49 | 6.9 | 7.2 | N/S | N/S | N/S | 8 | <8 | 840 | 156 | 2.23 | <0.25 | 8.05 | 0.95 | N/S | N/S | N/S | N/S | <0.04 | 0.0302 | <0.001 | 0.002 | 0.0088 | 0.18 | N/S | <0.02 | 0.0057 | N/S | <0.003 | <0.005 | <0.003 | 0.038 | <0.03 | <0.002 | <0.1 | N/S | 76.7 | 30.69 | 318 | N/S | N/S | N/S
2011-06-12 | 4.02 | 6.9 | 6.8 | 7 | 4 | N/S | <8 | <8 | 906 | 162 | 2.47 | <0.25 | 9.96 | 1.16 | N/S | N/S | N/S | N/S | <0.04 | 0.0336 | <0.001 | 0.0021 | 0.007 | 0.09 | N/S | <0.02 | 0.0057 | N/S | <0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 80.04 | 32.95 | 336 | N/S | N/S | N/S
2011-06-13 | 3.8 | 6.9 | 8.2 | 7 | 3 | <2 | <8 | <8 | 980 | 152 | 1.91 | 0.32 | 11.5 | 1.35 | <0.005 | <6 | 0.62 | 3600 | <0.04 | 0.035 | <0.001 | 0.0018 | 0.0068 | 0.19 | N/S | <0.02 | 0.0068 | N/S | <0.003 | <0.005 | <0.003 | 0.025 | <0.03 | <0.002 | <0.1 | N/S | 85.02 | 35.05 | 357 | N/S | N/S | N/S
2011-06-14 | 2.89 | 6.9 | 8.1 | 6 | 3 | N/S | <8 | <8 | 696 | 140 | 1.81 | <0.25 | 13.82 | 1.69 | N/S | N/S | N/S | N/S | <0.04 | 0.0337 | <0.001 | 0.0019 | 0.0067 | 0.09 | N/S | <0.02 | 0.0065 | <0.2 | <0.003 | <0.005 | <0.003 | 0.026 | <0.03 | <0.002 | <0.1 | <6 | 83.59 | 35.19 | 354 | N/S | 2.5 | 5.1
2011-06-15 | 3.76 | 7.1 | 7.4 | 7 | 4 | N/S | <8 | <8 | 672 | 138 | 1.8 | <0.25 | 13.01 | 1.68 | N/S | N/S | N/S | N/S | <0.04 | 0.0254 | <0.001 | 0.0026 | 0.0066 | 0.08 | N/S | <0.02 | 0.0056 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 67.21 | 26.89 | 279 | N/S | N/S | N/S
2011-06-16 | 4.33 | 6.9 | 8.2 | 8 | 4 | N/S | 12 | 11 | 718 | 142 | 2.34 | <0.25 | 9.98 | 1.26 | N/S | N/S | N/S | N/S | <0.04 | 0.0289 | <0.001 | 0.0026 | 0.0175 | 0.21 | N/S | <0.02 | 0.0224 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 65.11 | 26.31 | 271 | N/S | N/S | N/S
2011-06-17 | 4.31 | 6.9 | 8.3 | N/S | N/S | N/S | <8 | <8 | 942 | 196 | 1.95 | <0.25 | 10.54 | 1.07 | N/S | N/S | N/S | N/S | <0.04 | 0.0303 | <0.001 | 0.0024 | 0.0081 | 0.08 | N/S | <0.02 | 0.0051 | N/S | <0.003 | <0.005 | <0.003 | 0.067 | <0.03 | <0.002 | <0.1 | N/S | 75.01 | 28.97 | 307 | N/S | N/S | N/S
2011-06-18 | 3.58 | 6.9 | 7.3 | N/S | N/S | N/S | <8 | <8 | 976 | 194 | 1.99 | <0.25 | 11.77 | 1.42 | N/S | N/S | N/S | N/S | <0.04 | 0.0355 | <0.001 | 0.0022 | 0.0074 | 0.09 | N/S | <0.02 | 0.0085 | N/S | <0.003 | <0.005 | <0.003 | 0.046 | <0.03 | <0.002 | <0.1 | N/S | 88.38 | 34.37 | 362 | N/S | N/S | N/S
2011-06-19 | 3.11 | 6.9 | 7.1 | 8 | 4 | N/S | <8 | <8 | 1136 | 218 | 3.06 | 0.25 | 12.6 | 1.89 | N/S | N/S | N/S | N/S | <0.04 | 0.0403 | <0.001 | 0.0022 | 0.009 | 0.11 | N/S | <0.02 | 0.0172 | N/S | 0.0025 | <0.005 | <0.003 | 0.054 | <0.03 | <0.002 | <0.1 | N/S | 103.98 | 40.27 | 425 | N/S | N/S | N/S
2011-06-20 | 3.09 | 6.9 | 7.1 | 8 | 4 | <2 | <8 | <8 | 1062 | 228 | 1.99 | <0.25 | 12.31 | 1.85 | <0.005 | 8 | 0.65 | 89000 | <0.04 | 0.0344 | <0.001 | 0.0021 | 0.0092 | 0.09 | N/S | <0.02 | 0.0132 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 90.59 | 35.1 | 371 | N/S | N/S | N/S
2011-06-21 | 3.16 | 6.9 | 7.6 | 9 | 5 | N/S | <8 | <8 | 950 | 196 | 2.13 | <0.25 | 10.75 | 1.77 | N/S | N/S | N/S | N/S | <0.04 | 0.0328 | <0.001 | 0.002 | 0.0131 | 0.13 | N/S | <0.02 | 0.0108 | <0.2 | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | <6 | 87.06 | 34.74 | 360 | N/S | 3 | 6.6
2011-06-22 | 4.33 | 6.9 | 6.5 | 7 | 4 | N/S | <8 | <8 | 838 | 112 | 1.58 | <0.25 | 10.19 | 1.44 | N/S | N/S | N/S | N/S | <0.04 | 0.0285 | <0.001 | 0.0015 | 0.0126 | 0.25 | N/S | <0.02 | 0.0079 | N/S | 0.0033 | <0.005 | <0.003 | 0.06 | <0.03 | <0.002 | <0.1 | N/S | 79.87 | 33 | 335 | N/S | N/S | N/S
2011-06-23 | 3.77 | 6.9 | 7 | 6 | 5 | N/S | <8 | <8 | 1052 | 188 | 1.72 | <0.25 | 11.08 | 1.55 | N/S | N/S | N/S | N/S | <0.04 | 0.0323 | <0.001 | 0.0015 | 0.0124 | 0.1 | N/S | <0.02 | 0.0072 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 88.74 | 36.48 | 372 | N/S | N/S | N/S
2011-06-24 | 2.93 | 6.9 | 7.2 | N/S | N/S | N/S | <8 | <8 | 1124 | 220 | 3.02 | <0.25 | 12.04 | 1.8 | N/S | N/S | N/S | N/S | <0.04 | 0.0315 | <0.001 | 0.0016 | 0.0123 | 0.11 | N/S | <0.02 | 0.0069 | N/S | 0.0029 | <0.005 | <0.003 | 0.043 | <0.03 | <0.002 | <0.1 | N/S | 89.92 | 37.64 | 380 | N/S | N/S | N/S
2011-06-25 | 2.55 | 6.9 | 7.8 | N/S | N/S | N/S | <8 | <8 | 1080 | 198 | 2.58 | <0.25 | 12.95 | 2.02 | N/S | N/S | N/S | N/S | <0.04 | 0.0316 | <0.001 | 0.0019 | 0.0113 | 0.09 | N/S | <0.02 | 0.0071 | N/S | 0.0027 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 92.62 | 38.34 | 389 | N/S | N/S | N/S
2011-06-26 | 2.46 | 6.9 | 8.4 | 6 | 3 | N/S | <8 | <8 | 1107 | 208 | 2.56 | <0.25 | 13.63 | 2.23 | N/S | N/S | N/S | N/S | <0.04 | 0.0304 | <0.001 | 0.0015 | 0.0096 | 0.07 | N/S | <0.02 | 0.0086 | N/S | 0.0026 | <0.005 | <0.003 | 0.041 | <0.03 | <0.002 | <0.1 | N/S | 92.5 | 37.67 | 386 | N/S | N/S | N/S
2011-06-27 | 2.37 | 6.9 | 7 | 5 | 3 | <2 | <8 | <8 | 1077 | 196 | 2.79 | <0.25 | 13.81 | 2.06 | <0.005 | 6 | 0.8 | 2100 | <0.04 | 0.0298 | <0.001 | 0.0015 | 0.0078 | 0.09 | N/S | <0.02 | 0.009 | N/S | 0.0027 | <0.005 | <0.003 | 0.055 | <0.03 | <0.002 | <0.1 | N/S | 92.26 | 37.14 | 383 | N/S | N/S | N/S
2011-06-28 | 2.34 | 6.9 | 7.6 | 6 | 3 | N/S | <8 | <8 | 1038 | 180 | 2.29 | 1.41 | 14.28 | 2.18 | N/S | N/S | N/S | N/S | <0.04 | 0.0289 | <0.001 | 0.0015 | 0.0083 | 0.1 | N/S | <0.02 | 0.0092 | <0.2 | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | <6 | 89.66 | 36.53 | 374 | N/S | 3.9 | 5.4
2011-06-29 | 2.17 | 7 | 6.9 | 6 | 3 | N/S | <8 | <8 | 1017 | 122 | 2.53 | 0.31 | 16.22 | 2.41 | N/S | N/S | N/S | N/S | <0.04 | 0.028 | <0.001 | 0.0015 | 0.0091 | 0.07 | N/S | <0.02 | 0.0077 | N/S | 0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 89.02 | 36.46 | 372 | N/S | N/S | N/S
2011-06-30 | 1.94 | 6.9 | 6.8 | 6 | 3 | N/S | <8 | <8 | 1058 | 234 | 2.89 | 0.32 | 16.46 | 2.61 | N/S | N/S | N/S | N/S | <0.04 | 0.0302 | <0.001 | 0.0023 | 0.0077 | 0.09 | N/S | <0.02 | 0.0075 | N/S | 0.0027 | <0.005 | <0.003 | 0.041 | <0.03 | <0.002 | <0.1 | N/S | 93.13 | 37.07 | 385 | N/S | N/S | N/S
2011-07-01 | 2.21 | 7.1 | 6.6 | N/S | N/S | N/S | <8 | <8 | 1323 | 346 | 3.29 | 0.53 | 16.59 | 2.66 | N/S | N/S | N/S | N/S | <0.04 | 0.0376 | <0.001 | 0.002 | 0.0088 | 0.06 | N/S | <0.02 | 0.0097 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 115.53 | 39.97 | 453 | N/S | N/S | N/S
2011-07-02 | 2.02 | 7 | 6.8 | N/S | N/S | N/S | 9 | <8 | 1401 | 348 | 3.46 | 0.29 | 16.03 | 2.72 | N/S | N/S | N/S | N/S | <0.04 | 0.0404 | <0.001 | 0.0021 | 0.0097 | 0.13 | N/S | <0.02 | 0.0139 | N/S | 0.0025 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 116.39 | 39.74 | 454 | N/S | N/S | N/S
2011-07-03 | 2.37 | 6.9 | 7 | 7 | 4 | N/S | <8 | <8 | 1450 | 370 | 3.55 | 0.33 | 16.07 | 2.7 | N/S | N/S | N/S | N/S | <0.04 | 0.0431 | <0.001 | 0.0023 | 0.0089 | 0.09 | N/S | <0.02 | 0.0095 | N/S | 0.0029 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 123.53 | 43.1 | 486 | N/S | N/S | N/S
2011-07-04 | 1.86 | 6.9 | 6.9 | 8 | 4 | <2 | 8 | <8 | 1458 | 286 | 3.58 | 0.33 | 18.43 | 2.95 | <0.005 | 10 | 0.9 | N/S | <0.04 | 0.041 | <0.001 | 0.0015 | 0.008 | 0.08 | N/S | <0.02 | 0.0123 | N/S | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 119.27 | 40.99 | 467 | N/S | N/S | N/S
2011-07-05 | 2.32 | 6.8 | 7.4 | 9 | 5 | N/S | <8 | <8 | 1358 | 242 | 3.82 | 0.29 | 17.89 | 3.01 | N/S | N/S | N/S | 260000 | <0.04 | 0.0385 | <0.001 | 0.0017 | 0.0075 | 0.08 | 0.026 | <0.02 | 0.0152 | <0.2 | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | <6 | 112.06 | 40.36 | 446 | T/X | <0.5 | 5.5
2011-07-06 | 1.95 | 6.9 | 6.2 | 8 | 5 | N/S | <8 | <8 | 1362 | 242 | 3.68 | 0.32 | 18.2 | 2.63 | N/S | N/S | N/S | N/S | <0.04 | 0.0393 | <0.001 | <0.002 | 0.0069 | 0.12 | N/S | <0.02 | 0.0122 | N/S | <0.003 | <0.005 | <0.003 | 0.049 | <0.03 | <0.002 | <0.1 | N/S | 119.67 | 43.41 | 478 | N/S | N/S | N/S
2011-07-07 | 2.03 | 6.9 | 7.1 | 7 | 4 | N/S | <8 | <8 | 1354 | 332 | 2.91 | 0.27 | 18.74 | 2.5 | N/S | N/S | N/S | N/S | <0.04 | 0.0345 | <0.001 | 0.0017 | 0.007 | 0.07 | N/S | <0.02 | 0.0085 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 104.37 | 40.09 | 426 | N/S | N/S | N/S
2011-07-08 | 1.85 | 6.9 | 7.1 | N/S | N/S | N/S | <8 | <8 | 1357 | 366 | 2.26 | 0.3 | 19.29 | 2.88 | N/S | N/S | N/S | N/S | <0.04 | 0.0334 | <0.001 | 0.0016 | 0.0079 | 0.11 | N/S | <0.02 | 0.0093 | N/S | <0.003 | <0.005 | <0.003 | 0.053 | <0.03 | <0.002 | <0.1 | N/S | 103.07 | 40.25 | 423 | N/S | N/S | N/S
2011-07-09 | 1.8 | 6.8 | 6.7 | N/S | N/S | N/S | <8 | <8 | 1303 | 344 | 2.86 | 0.53 | 20.08 | 3.18 | N/S | N/S | N/S | N/S | <0.04 | 0.0331 | <0.001 | 0.002 | 0.0112 | 0.07 | N/S | <0.02 | 0.0135 | N/S | <0.003 | <0.005 | <0.003 | 0.064 | <0.03 | <0.002 | <0.1 | N/S | 104.31 | 40.71 | 428 | N/S | N/S | N/S
2011-07-10 | 1.77 | 6.9 | 6 | 9 | 4 | N/S | <8 | <8 | 1250 | 318 | 2.58 | 0.49 | 19.94 | 3.32 | N/S | N/S | N/S | N/S | <0.04 | 0.0313 | <0.001 | 0.002 | 0.0113 | 0.1 | N/S | <0.02 | 0.0169 | N/S | <0.003 | <0.005 | <0.003 | 0.097 | <0.03 | <0.002 | <0.1 | N/S | 97.8 | 38.29 | 402 | N/S | N/S | N/S
2011-07-11 | 1.99 | 6.8 | 6.5 | 8 | 5 | <2 | <8 | <8 | 1090 | 250 | 2.95 | 0.27 | 20.4 | 3.21 | 0.005 | 6 | 0.93 | 110000 | <0.04 | 0.0293 | <0.001 | 0.0023 | 0.0105 | 0.09 | N/S | <0.02 | 0.0134 | N/S | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 90.37 | 34.11 | 366 | N/S | N/S | N/S
2011-07-12 | 2.16 | 7.2 | 7 | 7 | 4 | N/S | <8 | <8 | 922 | 124 | 2.62 | 1.55 | 18.56 | 2.91 | N/S | N/S | N/S | N/S | <0.04 | 0.025 | <0.001 | 0.0018 | 0.0099 | 0.07 | N/S | <0.02 | 0.0101 | <0.2 | <0.003 | <0.005 | <0.003 | 0.044 | <0.03 | <0.002 | <0.1 | <6 | 73.08 | 28.8 | 301 | N/S | 8.5 | 6.7
2011-07-13 | 1.85 | 7.3 | 8.3 | 7 | 4 | N/S | <8 | <8 | 978 | 160 | 2.27 | 0.25 | 19.75 | 2.93 | N/S | N/S | N/S | N/S | <0.04 | 0.0264 | <0.001 | 0.0027 | 0.0095 | 0.08 | N/S | <0.02 | 0.0086 | N/S | 0.0025 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 79.44 | 30.93 | 326 | N/S | N/S | N/S
2011-07-14 | 1.73 | 7.2 | 7.8 | 5 | 3 | N/S | <8 | <8 | 974 | 154 | 2.22 | <0.25 | 21.19 | 3.12 | N/S | N/S | N/S | N/S | <0.04 | 0.0264 | <0.001 | 0.0017 | 0.0098 | 0.08 | N/S | <0.02 | 0.008 | N/S | 0.0026 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 82.75 | 31.89 | 338 | N/S | N/S | N/S
2011-07-15 | 1.67 | 7.2 | 6.6 | N/S | N/S | N/S | <8 | <8 | 1054 | 268 | 1.7 | <0.25 | 22.25 | 3.28 | N/S | N/S | N/S | N/S | <0.04 | 0.0228 | <0.001 | 0.0015 | 0.0052 | 0.05 | N/S | <0.02 | 0.0057 | N/S | <0.003 | <0.005 | <0.003 | 0.057 | <0.03 | <0.002 | <0.1 | N/S | 76.09 | 27.39 | 303 | N/S | N/S | N/S
2011-07-16 | 1.49 | 7.1 | 7.3 | N/S | N/S | N/S | <8 | <8 | 1006 | 260 | 1.22 | 0.26 | 23.49 | 3.5 | N/S | N/S | N/S | N/S | <0.04 | 0.024 | <0.001 | <0.002 | 0.0057 | 0.07 | N/S | <0.02 | 0.0068 | N/S | <0.003 | <0.005 | <0.003 | 0.066 | <0.03 | <0.002 | <0.1 | N/S | 81.59 | 29.25 | 324 | N/S | N/S | N/S
2011-07-17 | 2.13 | 6.9 | 7 | 7 | 3 | N/S | <8 | <8 | 994 | 230 | 2.78 | 1.42 | 21.69 | 3.64 | N/S | N/S | N/S | N/S | <0.04 | 0.0244 | <0.001 | 0.0017 | 0.0069 | 0.08 | N/S | <0.02 | 0.0133 | N/S | <0.003 | <0.005 | <0.003 | 0.049 | <0.03 | <0.002 | <0.1 | N/S | 79.05 | 28.61 | 315 | N/S | N/S | N/S
2011-07-18 | 1.92 | 6.8 | 6.1 | 6 | 2 | 2.1 | <8 | <8 | 900 | 136 | 2.5 | 0.68 | 20.36 | 3.39 | 0.008 | <6 | 1 | 27000 | <0.04 | 0.0248 | <0.001 | 0.0018 | 0.0067 | 0.06 | N/S | <0.02 | 0.0118 | N/S | <0.003 | <0.005 | <0.003 | 0.052 | <0.03 | <0.002 | <0.1 | N/S | 76.01 | 28.81 | 308 | N/S | N/S | N/S
2011-07-19 | 1.92 | 6.8 | 7.5 | 5 | 3 | N/S | <8 | <8 | 932 | 120 | 2.11 | 0.33 | 20.76 | 3.33 | N/S | N/S | N/S | N/S | <0.04 | 0.0253 | <0.001 | 0.0019 | 0.0062 | 0.06 | N/S | <0.02 | 0.0107 | <0.2 | <0.003 | <0.005 | <0.003 | 0.057 | <0.03 | <0.002 | <0.1 | <6 | 77.56 | 28.96 | 313 | N/S | <0.5 | 6.4
2011-07-20 | 1.75 | 6.7 | 7 | 6 | 3 | N/S | <8 | <8 | 928 | 158 | 2.5 | 0.26 | 21.26 | 3.48 | N/S | N/S | N/S | N/S | <0.04 | 0.0271 | <0.001 | 0.002 | 0.0073 | 0.08 | N/S | <0.02 | 0.0149 | N/S | <0.003 | <0.005 | <0.003 | 0.056 | <0.03 | <0.002 | <0.1 | N/S | 82.97 | 30.21 | 332 | N/S | N/S | N/S
2011-07-21 | 1.74 | 6.9 | 5.8 | 4 | 2 | N/S | <8 | <8 | 1217 | 286 | 2.54 | 0.83 | 21.27 | 3.28 | N/S | N/S | N/S | N/S | <0.04 | 0.0367 | <0.001 | <0.002 | 0.0068 | 0.09 | N/S | <0.02 | 0.014 | N/S | <0.003 | <0.005 | <0.003 | 0.061 | <0.03 | <0.002 | <0.1 | N/S | 115.45 | 36.51 | 439 | N/S | N/S | N/S
2011-07-22 | 2.33 | 6.8 | 7 | N/S | N/S | N/S | <8 | <8 | 1304 | 328 | 2.3 | <0.25 | 18.41 | 2.63 | N/S | N/S | N/S | N/S | <0.04 | 0.0369 | <0.001 | <0.002 | 0.007 | 0.14 | N/S | <0.02 | 0.0093 | N/S | <0.003 | <0.005 | <0.003 | 0.047 | <0.03 | <0.002 | <0.1 | N/S | 113.09 | 35.69 | 429 | N/S | N/S | N/S
2011-07-23 | 3.84 | 6.9 | 7.2 | N/S | N/S | N/S | 8 | <8 | 802 | 182 | 1.44 | <0.25 | 10.03 | 1.52 | N/S | N/S | N/S | N/S | <0.04 | 0.0262 | <0.001 | <0.002 | 0.0073 | 0.09 | N/S | <0.02 | 0.0085 | N/S | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | N/S | 73.51 | 26.07 | 291 | N/S | N/S | N/S
2011-07-24 | 4.24 | 6.6 | 8 | 6 | 3 | N/S | 8 | <8 | 692 | 140 | 1.14 | <0.25 | 7.65 | 1.13 | N/S | N/S | N/S | N/S | <0.04 | 0.0256 | 0.0014 | 0.002 | 0.0076 | 0.16 | N/S | <0.02 | 0.0104 | N/S | <0.003 | <0.005 | <0.003 | 0.028 | <0.03 | <0.002 | <0.1 | N/S | 62.88 | 23.66 | 254 | N/S | N/S | N/S
2011-07-25 | 4.26 | 6.3 | 7.8 | 3 | <2 | <2 | <8 | <8 | 718 | 132 | 1.19 | <0.25 | 7.67 | 0.94 | <0.005 | <6 | 0.45 | 11000 | <0.04 | 0.0285 | <0.001 | 0.0015 | 0.0054 | 0.07 | N/S | <0.02 | 0.0051 | N/S | <0.003 | <0.005 | <0.003 | 0.03 | <0.03 | <0.002 | <0.1 | N/S | 71.57 | 27.57 | 292 | N/S | N/S | N/S
2011-07-26 | 4.14 | 6.5 | 6.6 | 3 | <2 | N/S | <8 | <8 | 944 | 178 | 1.32 | <0.25 | 10.24 | 1.2 | N/S | N/S | N/S | N/S | <0.04 | 0.0324 | <0.001 | 0.0029 | 0.0043 | 0.09 | N/S | <0.02 | 0.0047 | <0.2 | <0.003 | <0.005 | <0.003 | 0.031 | <0.03 | <0.002 | <0.1 | <6 | 81.89 | 31.91 | 336 | N/S | <2.5 | 5.4
2011-07-27 | 3.03 | 7.5 | 8.1 | 3 | <2 | N/S | <8 | <8 | 1130 | 262 | 1.25 | <0.25 | 14.25 | 1.66 | N/S | N/S | N/S | N/S | <0.04 | 0.0352 | <0.001 | 0.0018 | 0.0058 | 0.09 | N/S | <0.02 | 0.0045 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 90.69 | 35.37 | 372 | N/S | N/S | N/S
2011-07-28 | 3.47 | 7.5 | 6.3 | 4 | 2 | N/S | <8 | <8 | 858 | 156 | 0.95 | <0.25 | 12.52 | 1.75 | N/S | N/S | N/S | N/S | <0.04 | 0.0314 | <0.001 | 0.0016 | 0.0062 | 0.09 | N/S | <0.02 | 0.0048 | N/S | <0.003 | <0.005 | <0.003 | 0.042 | <0.03 | <0.002 | <0.1 | N/S | 80.86 | 31.13 | 330 | N/S | N/S | N/S
2011-07-29 | 3.28 | 7.6 | 6.5 | N/S | N/S | N/S | <8 | <8 | 998 | 204 | 2.29 | <0.25 | 11.72 | 1.54 | N/S | N/S | N/S | N/S | <0.04 | 0.0349 | <0.001 | 0.0019 | 0.0075 | 0.11 | N/S | <0.02 | 0.006 | N/S | <0.003 | <0.005 | <0.003 | 0.034 | <0.03 | <0.002 | <0.1 | N/S | 88.37 | 31.91 | 352 | N/S | N/S | N/S
2011-07-30 | 3.25 | 7.4 | 7.4 | N/S | N/S | N/S | <8 | <8 | 1190 | 248 | 2.77 | 0.34 | 12.61 | 1.7 | N/S | N/S | N/S | N/S | <0.04 | 0.0426 | <0.001 | 0.0019 | 0.007 | 0.11 | N/S | <0.02 | 0.0181 | N/S | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | N/S | 103.75 | 35.89 | 407 | N/S | N/S | N/S
2011-07-31 | 2.25 | 7.5 | 7.3 | 4 | 2 | N/S | <8 | <8 | 1287 | 250 | 3.71 | 0.37 | 15.01 | 2.11 | N/S | N/S | N/S | N/S | <0.04 | 0.0384 | <0.001 | <0.002 | 0.0061 | 0.07 | N/S | <0.02 | 0.0093 | N/S | <0.003 | <0.005 | <0.003 | 0.032 | <0.03 | <0.002 | <0.1 | N/S | 99.58 | 35.91 | 397 | N/S | N/S | N/S
2011-08-01 | 2.07 | 7.3 | 7.1 | 5 | 2 | <2 | <8 | <8 | 1190 | 240 | 3.64 | 0.57 | 16.41 | 2.57 | 0.005 | <6 | 0.81 | 3800 | <0.04 | 0.0362 | <0.001 | <0.002 | 0.0053 | 0.08 | N/S | <0.02 | 0.0066 | N/S | <0.003 | <0.005 | <0.003 | 0.031 | <0.03 | <0.002 | <0.1 | N/S | 97.39 | 36.28 | 393 | N/S | N/S | N/S
2011-08-02 | 2.16 | 7.2 | 7.1 | 5 | 3 | N/S | <8 | <8 | 1290 | 240 | 3.36 | <0.25 | 17.96 | 2.73 | N/S | N/S | N/S | N/S | <0.04 | 0.0349 | <0.001 | <0.002 | 0.0088 | 0.08 | 0.027 | <0.02 | 0.0069 | <0.2 | <0.003 | <0.005 | <0.003 | 0.033 | <0.03 | <0.002 | <0.1 | <6 | 97.45 | 37.33 | 397 | T/X | 0.7 | 5.5
2011-08-03 | 2.28 | 7.5 | 5.8 | 5 | 2 | N/S | <8 | <8 | 1126 | 198 | 2.61 | 0.25 | 17.86 | 2.61 | N/S | N/S | N/S | N/S | <0.04 | 0.0298 | <0.001 | 0.0019 | 0.0085 | 0.09 | N/S | <0.02 | 0.0057 | N/S | 0.0029 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 86.29 | 33.24 | 352 | N/S | N/S | N/S
2011-08-04 | 2.05 | 7.5 | 6 | 4 | <2 | N/S | <8 | <8 | 1206 | 248 | 2.97 | 0.28 | 18.71 | 2.76 | N/S | N/S | N/S | N/S | <0.04 | 0.0297 | <0.001 | 0.0017 | 0.0095 | 0.06 | N/S | <0.02 | 0.0062 | N/S | 0.0028 | <0.005 | <0.003 | 0.046 | <0.03 | <0.002 | <0.1 | N/S | 88.25 | 34.11 | 361 | N/S | N/S | N/S
2011-08-05 | 1.87 | 7.5 | 5.8 | N/S | N/S | N/S | <8 | <8 | 1175 | 222 | 3.33 | 0.28 | 19.63 | 2.66 | N/S | N/S | N/S | N/S | <0.04 | 0.0316 | <0.001 | 0.0016 | 0.0111 | 0.1 | N/S | <0.02 | 0.007 | N/S | 0.0029 | <0.005 | <0.003 | 0.055 | <0.03 | <0.002 | <0.1 | N/S | 91.89 | 35.55 | 376 | N/S | N/S | N/S
2011-08-06 | 2.48 | 7.4 | 6.4 | N/S | N/S | N/S | <8 | <8 | 1083 | 226 | 3.06 | <0.25 | 17.32 | 2.48 | N/S | N/S | N/S | N/S | <0.04 | 0.0312 | <0.001 | 0.002 | 0.0073 | 0.09 | N/S | <0.02 | 0.0075 | N/S | <0.003 | <0.005 | <0.003 | 0.039 | <0.03 | <0.002 | <0.1 | N/S | 91.96 | 35.12 | 374 | N/S | N/S | N/S
2011-08-07 | 2.47 | 7.5 | 6.2 | 4 | <2 | N/S | <8 | <8 | 1025 | 198 | 3.24 | 0.29 | 16.14 | 2.27 | N/S | N/S | N/S | N/S | <0.04 | 0.0302 | <0.001 | 0.0022 | 0.0061 | 0.11 | N/S | 0.016 | 0.0096 | N/S | <0.003 | <0.005 | <0.003 | 0.045 | <0.03 | <0.002 | <0.1 | N/S | 88.85 | 33.73 | 361 | N/S | N/S | N/S
2011-08-08 | 2.2 | 7.8 | 7.2 | 5 | 3 | <2 | <8 | <8 | 1022 | 196 | 3.19 | 0.27 | 16.5 | 2.35 | <0.005 | <6 | 0.82 | 2000 | <0.04 | 0.0293 | <0.001 | 0.0022 | 0.0071 | 0.11 | N/S | <0.02 | 0.0081 | N/S | <0.003 | <0.005 | <0.003 | 0.053 | <0.03 | <0.002 | <0.1 | N/S | 89 | 33.51 | 360 | N/S | N/S | N/S
2011-08-09 | 3.05 | 7.8 | 7.2 | 4 | 2 | N/S | <8 | <8 | 968 | 252 | 2.84 | 0.27 | 14.81 | 2.06 | N/S | N/S | N/S | N/S | <0.04 | 0.0276 | <0.001 | 0.0018 | 0.0062 | 0.09 | N/S | <0.02 | 0.0073 | <0.2 | <0.003 | <0.005 | <0.003 | 0.046 | <0.03 | <0.002 | <0.1 | <6 | 81.6 | 30.67 | 330 | N/S | <2.5 | 6.3
2011-08-10 | 2.01 | 7.8 | 7 | 6 | 3 | N/S | <8 | <8 | 996 | 198 | 2.92 | 0.36 | 16.76 | 2.44 | N/S | N/S | N/S | N/S | <0.04 | 0.0298 | <0.001 | 0.0016 | 0.0063 | 0.1 | N/S | <0.02 | 0.0092 | N/S | <0.003 | <0.005 | <0.003 | 0.031 | <0.03 | <0.002 | <0.1 | N/S | 83.47 | 32.62 | 343 | N/S | N/S | N/S
2011-08-11 | 1.89 | 7.6 | 7.2 | 4 | <2 | N/S | <8 | <8 | 1080 | 236 | 2.73 | 0.25 | 20.68 | 2.78 | N/S | N/S | N/S | N/S | <0.04 | 0.0297 | <0.001 | 0.0017 | 0.0061 | 0.05 | N/S | <0.02 | 0.0067 | N/S | <0.003 | <0.005 | <0.003 | 0.032 | <0.03 | <0.002 | <0.1 | N/S | 89.53 | 34.06 | 364 | N/S | N/S | N/S
2011-08-12 | 1.77 | 7.6 | 6.3 | N/S | N/S | N/S | <8 | <8 | 1022 | 192 | 2.74 | 0.28 | 21.3 | 3.31 | N/S | N/S | N/S | N/S | <0.04 | 0.0311 | <0.001 | 0.0016 | 0.0078 | 0.06 | N/S | <0.02 | 0.0069 | N/S | <0.003 | <0.005 | <0.003 | 0.037 | <0.03 | <0.002 | <0.1 | N/S | 93.88 | 35.47 | 381 | N/S | N/S | N/S
2011-08-13 | 1.95 | 7.6 | 7.2 | N/S | N/S | N/S | <8 | <8 | 1231 | 280 | 3.37 | <0.25 | 21.5 | 3.34 | N/S | N/S | N/S | N/S | <0.04 | 0.038 | <0.001 | 0.002 | 0.007 | 0.06 | N/S | <0.02 | 0.0082 | N/S | <0.003 | <0.005 | <0.003 | 0.05 | <0.03 | <0.002 | <0.1 | N/S | 118.7 | 38.49 | 455 | N/S | N/S | N/S
2011-08-14 | 2.32 | 7.6 | 7.5 | 4 | 3 | N/S | <8 | <8 | 1190 | 260 | 3.29 | <0.25 | 18.52 | 2.86 | N/S | N/S | N/S | N/S | <0.04 | 0.034 | <0.001 | 0.0024 | 0.009 | 0.08 | N/S | <0.02 | 0.008 | N/S | <0.003 | <0.005 | <0.003 | 0.068 | <0.03 | <0.002 | <0.1 | N/S | 102.62 | 33.55 | 394 | N/S | N/S | N/S
2011-08-15 | 2.56 | 7.8 | 7.6 | 6 | 3 | 2.8 | <8 | <8 | 1239 | 198 | 2.41 | 0.54 | 17.61 | 2.83 | <0.005 | 6 | 0.87 | 45000 | <0.04 | 0.0353 | <0.001 | 0.0022 | 0.0095 | 0.07 | N/S | <0.02 | 0.0099 | N/S | <0.003 | <0.005 | <0.003 | 0.056 | <0.03 | <0.002 | <0.1 | N/S | 101.8 | 35 | 398 | N/S | N/S | N/S
2011-08-16 | 1.97 | 7.7 | 6.6 | 5 | 3 | N/S | <8 | <8 | 1296 | 226 | 1.9 | 0.42 | 18.88 | 2.91 | N/S | N/S | N/S | N/S | <0.04 | 0.036 | <0.001 | 0.002 | 0.0081 | 0.06 | N/S | <0.02 | 0.0094 | <0.2 | <0.003 | <0.005 | <0.003 | 0.061 | <0.03 | <0.002 | <0.1 | <6 | 105.07 | 37.05 | 415 | N/S | <2.5 | 7.7
2011-08-17 | 1.94 | 7.8 | 6.5 | 6 | 4 | N/S | <8 | <8 | 1359 | 246 | 5.11 | 0.58 | 19.55 | 3.28 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0103 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 100.64 | 35.2 | 396 | N/S | N/S | N/S
2011-08-18 | 1.81 | 7.5 | 6 | 7 | 4 | N/S | <8 | <8 | 1423 | 308 | 3.6 | 0.52 | 21.68 | 4 | N/S | N/S | N/S | N/S | <0.05 | 0.0384 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0141 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 106.76 | 37.13 | 419 | N/S | N/S | N/S
2011-08-19 | 1.9 | 7.4 | 6.1 | N/S | N/S | N/S | <8 | <8 | 1453 | 370 | 3.2 | <0.25 | 21.04 | 3.6 | N/S | N/S | N/S | N/S | <0.05 | 0.0366 | <0.001 | <0.01 | <0.02 | 0.2 | N/S | <0.03 | 0.0119 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 104.15 | 36.46 | 410 | N/S | N/S | N/S
2011-08-20 | 1.94 | 7.4 | 6.8 | N/S | N/S | N/S | <8 | <8 | 1304 | 334 | 3.55 | <0.25 | 18.38 | 3.45 | N/S | N/S | N/S | N/S | <0.05 | 0.0333 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0103 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 96.72 | 34.22 | 382 | N/S | N/S | N/S
2011-08-21 | 2.13 | 7.2 | 7 | 7 | 3 | N/S | <8 | <8 | 1118 | 270 | 3.43 | <0.25 | 16.57 | 2.81 | N/S | N/S | N/S | N/S | <0.05 | 0.0309 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0081 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 93.84 | 34.1 | 375 | N/S | N/S | N/S
2011-08-22 | 2.1 | 7.3 | 6.2 | 7 | 3 | 2.6 | <8 | <8 | 1072 | 196 | 2.78 | <0.25 | 18.38 | 2.72 | <0.005 | <6 | 0.88 | 15000 | <0.05 | 0.0312 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0143 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 92.75 | 33.84 | 371 | N/S | N/S | N/S
2011-08-23 | 2.43 | 7.2 | 7 | 7 | 3 | N/S | 8 | <8 | 858 | 162 | 2.92 | <0.25 | 16.29 | 2.48 | N/S | N/S | N/S | N/S | <0.05 | 0.0273 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0095 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 77.95 | 28.2 | 311 | N/S | <2.5 | 6.1
2011-08-24 | 3.01 | 7.3 | 7.2 | 8 | 4 | N/S | <8 | <8 | 768 | 142 | 3.9 | <0.25 | 11.25 | 1.71 | N/S | N/S | N/S | N/S | <0.05 | 0.0271 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0073 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 76.33 | 28.31 | 307 | N/S | N/S | N/S
2011-08-25 | 2.53 | 7.5 | 7.1 | 8 | 4 | N/S | <8 | <8 | 950 | 242 | 2.2 | <0.25 | 15.32 | 2.12 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0083 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 79.42 | 29.4 | 319 | N/S | N/S | N/S
2011-08-26 | 1.86 | 7.5 | 6.8 | N/S | N/S | N/S | <8 | <8 | 1209 | 250 | 2.68 | <0.25 | 18.28 | 2.64 | N/S | N/S | N/S | N/S | <0.05 | 0.0408 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0097 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 111.52 | 35.1 | 423 | N/S | N/S | N/S
2011-08-27 | 1.76 | 7.5 | 7.5 | N/S | N/S | N/S | <8 | <8 | 1250 | 248 | 2.74 | <0.25 | 20.28 | 3.03 | N/S | N/S | N/S | N/S | <0.05 | 0.0396 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.014 | N/S | <0.008 | 0.007 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 109.48 | 35.65 | 420 | N/S | N/S | N/S
2011-08-28 | 1.73 | 7.5 | 7.6 | 7 | 3 | N/S | <8 | <8 | 1289 | 256 | 2.27 | 0.3 | 20.2 | 3.21 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0141 | N/S | <0.008 | 0.007 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 101.45 | 34.04 | 394 | N/S | N/S | N/S
2011-08-29 | 1.6 | 7.5 | 7 | 7 | 3 | 3.5 | 8 | 8 | 1330 | 278 | 3.24 | <0.25 | 20.77 | 3.02 | 0.006 | <6 | 0.97 | 1600 | <0.05 | 0.0364 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0112 | N/S | <0.008 | 0.008 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 105.27 | 35.64 | 410 | N/S | N/S | N/S
2011-08-30 | 1.62 | 7.5 | 7.5 | 8 | 4 | N/S | 11 | <8 | 1393 | 318 | 3.15 | <0.25 | 22.69 | 3.29 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.024 | <0.2 | <0.008 | 0.009 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 106.23 | 36.36 | 415 | N/S | <2.5 | 5.5
2011-08-31 | 1.94 | 7.5 | 6.6 | 5 | 3 | N/S | <8 | <8 | 1300 | 264 | 2.74 | <0.25 | 21.2 | 3.19 | N/S | N/S | N/S | N/S | <0.05 | 0.0325 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0088 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 94.17 | 32.75 | 370 | N/S | N/S | N/S
2011-09-01 | 1.79 | 7.5 | 6.6 | 6 | 3 | N/S | <8 | <8 | 1453 | 390 | 3.44 | <0.25 | 19.89 | 3.17 | N/S | N/S | N/S | N/S | <0.05 | 0.0338 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0085 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 99.07 | 34.1 | 388 | N/S | N/S | N/S
2011-09-02 | 1.69 | 7.4 | 6.5 | N/S | N/S | N/S | 8 | <8 | 1272 | 222 | 4.81 | <0.25 | 19.64 | 3.33 | N/S | N/S | N/S | N/S | <0.05 | 0.0358 | <0.001 | <0.01 | <0.02 | 0.21 | N/S | <0.03 | 0.0335 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 96.93 | 34 | 382 | N/S | N/S | N/S
2011-09-03 | 1.98 | 7.5 | 6.5 | N/S | N/S | N/S | <8 | <8 | 1125 | 196 | 4.19 | <0.25 | 18.93 | 3.03 | N/S | N/S | N/S | N/S | <0.05 | 0.0302 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0079 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 89.52 | 31.8 | 354 | N/S | N/S | N/S
2011-09-04 | 2.74 | 7.4 | 6.2 | 4 | 2 | N/S | <8 | <8 | 896 | 154 | 1.59 | <0.25 | 13.06 | 2.13 | N/S | N/S | N/S | N/S | <0.05 | 0.0259 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0064 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 76.76 | 27.76 | 306 | N/S | N/S | N/S
2011-09-05 | 2.51 | 7.5 | 7.6 | 3 | 3 | <2 | <8 | <8 | 1039 | 200 | 2.37 | <0.25 | 16.63 | 2.16 | 0.007 | <6 | 0.79 | N/S | <0.05 | 0.0306 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0076 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 88.03 | 32.46 | 353 | N/S | N/S | N/S
2011-09-06 | 1.93 | 7.4 | 6 | 4 | 3 | N/S | <8 | <8 | 1055 | 176 | 4.47 | <0.25 | 18.95 | 2.4 | N/S | N/S | N/S | 6400 | <0.05 | 0.0318 | <0.001 | <0.01 | <0.02 | <0.2 | <0.2 | <0.03 | 0.0079 | <0.2 | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 92.49 | 33.49 | 369 | T/X | <2.5 | 5.4
2011-09-07 | 1.65 | 7.5 | 7 | 3 | <2 | N/S | <8 | <8 | 1143 | 204 | 3.91 | <0.25 | 21.04 | 2.96 | N/S | N/S | N/S | N/S | <0.05 | 0.0309 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0081 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.94 | 32.6 | 361 | N/S | N/S | N/S
2011-09-08 | 1.65 | 7.6 | 8.7 | 3 | 2 | N/S | <8 | <8 | 1134 | 224 | 2 | <0.25 | 22.62 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.0299 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0082 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.07 | 31.96 | 357 | N/S | N/S | N/S
2011-09-09 | 1.74 | 7.4 | 7.2 | N/S | N/S | N/S | <8 | <8 | 1086 | 210 | 3.19 | <0.25 | 22.95 | 3.19 | N/S | N/S | N/S | N/S | <0.05 | 0.0279 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 84.31 | 30.17 | 335 | N/S | N/S | N/S
2011-09-10 | 1.8 | 7.6 | 7.8 | N/S | N/S | N/S | <8 | <8 | 972 | 164 | 2.09 | <0.25 | 22.29 | 3.19 | N/S | N/S | N/S | N/S | <0.05 | 0.0263 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.008 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 78.46 | 28.68 | 314 | N/S | N/S | N/S
2011-09-11 | 1.71 | 7.6 | 7.4 | 4 | 2 | N/S | <8 | <8 | 936 | 158 | 2.76 | <0.25 | 21.64 | 3.28 | N/S | N/S | N/S | N/S | <0.05 | 0.0255 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0086 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 76.03 | 27.88 | 305 | N/S | N/S | N/S
2011-09-12 | 1.82 | 7.6 | 7.3 | 4 | 3 | 2.4 | <8 | <8 | 918 | 160 | 2.41 | <0.25 | 22.19 | 3.37 | 0.007 | <6 | 1.01 | 7400 | <0.05 | 0.025 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0086 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 74.47 | 27.23 | 298 | N/S | N/S | N/S
2011-09-13 | 1.69 | 7.6 | 7.1 | 4 | 3 | N/S | <8 | <8 | 1074 | 154 | 2.11 | <0.25 | 22.6 | 3.43 | N/S | N/S | N/S | N/S | <0.05 | 0.0329 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0089 | <0.2 | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 103.25 | 32.55 | 392 | N/S | <2.5 | 5.7
2011-09-14 | 1.72 | 7.4 | 6.7 | 5 | 3 | N/S | <8 | <8 | 1281 | 266 | 2.3 | <0.25 | 24.08 | 3.68 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0175 | N/S | <0.008 | <0.005 | <0.004 | 0.061 | <0.05 | <0.001 | <0.02 | N/S | 111.74 | 34.26 | 420 | N/S | N/S | N/S
2011-09-15 | 1.68 | 7.5 | 7.2 | <2 | <2 | N/S | <8 | <8 | 1567 | 426 | 2.06 | 0.72 | 22.24 | 3.16 | N/S | N/S | N/S | N/S | <0.05 | 0.0382 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.013 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 117.16 | 36.89 | 444 | N/S | N/S | N/S
2011-09-16 | 1.65 | 7.4 | 7 | N/S | N/S | N/S | <8 | <8 | 1535 | 324 | 1.47 | <0.25 | 22.21 | 3.23 | N/S | N/S | N/S | N/S | <0.05 | 0.0399 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0135 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 122.57 | 38.58 | 465 | N/S | N/S | N/S
2011-09-17 | 1.72 | 7.6 | 7.3 | N/S | N/S | N/S | <8 | <8 | 1500 | 278 | 1.24 | 0.46 | 21.74 | 3.24 | N/S | N/S | N/S | N/S | <0.05 | 0.0376 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0263 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 112.73 | 36.34 | 431 | N/S | N/S | N/S
2011-09-18 | 1.97 | 7.5 | 7.6 | 8 | 5 | N/S | <8 | <8 | 1386 | 220 | <0.45 | 0.86 | 18.41 | 2.69 | N/S | N/S | N/S | N/S | <0.05 | 0.0343 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0406 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 103.05 | 33.94 | 397 | N/S | N/S | N/S
2011-09-19 | 2.65 | 7.4 | 6.5 | 5 | 3 | 2.1 | <8 | <8 | 946 | 152 | 2.01 | <0.25 | 11.5 | 2.01 | 0.006 | <6 | 0.74 | 24000 | <0.05 | 0.0245 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0149 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 70.19 | 24.96 | 278 | N/S | N/S | N/S
2011-09-20 | 2.65 | 7.5 | 7 | 7 | 5 | N/S | <8 | <8 | 1076 | 204 | 2.05 | <0.25 | 18.94 | 2.86 | N/S | N/S | N/S | N/S | <0.05 | 0.0276 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0118 | <0.2 | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 81.72 | 29.55 | 326 | N/S | <2.5 | 5.9
2011-09-21 | 2.14 | 7.5 | 7.2 | 6 | 4 | N/S | <8 | <8 | 1152 | 178 | 1.72 | <0.25 | 20.23 | 2.99 | N/S | N/S | N/S | N/S | <0.05 | 0.0298 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0104 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 87.11 | 31.86 | 349 | N/S | N/S | N/S
2011-09-22 | 1.77 | 7.4 | 6.9 | 5 | 3 | N/S | <8 | <8 | 1235 | 220 | 2.22 | <0.25 | 22.89 | 3.39 | N/S | N/S | N/S | N/S | <0.05 | 0.0291 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0076 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 89.38 | 32.4 | 357 | N/S | N/S | N/S
2011-09-23 | 1.83 | 7.4 | 6.5 | N/S | N/S | N/S | <8 | <8 | 1443 | 294 | 2.97 | <0.25 | 24.14 | 3.45 | N/S | N/S | N/S | N/S | <0.05 | 0.0341 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.008 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 103.75 | 33.57 | 397 | N/S | N/S | N/S
2011-09-24 | 2.02 | 7.6 | 7.4 | N/S | N/S | N/S | <8 | <8 | 1494 | 274 | 2.2 | <0.25 | 23.09 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.0357 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0097 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 107.27 | 33.86 | 407 | N/S | N/S | N/S
2011-09-25 | 1.85 | 7.6 | 7.9 | 5 | 4 | N/S | <8 | <8 | 1508 | 286 | 2.72 | 0.32 | 22.2 | 3.24 | N/S | N/S | N/S | N/S | <0.05 | 0.0323 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0118 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 95.58 | 32.07 | 371 | N/S | N/S | N/S
2011-09-26 | 3.53 | 7.6 | 7.3 | 6 | 4 | <2 | <8 | <8 | 986 | 150 | 1.93 | <0.25 | 14.3 | 2.21 | 0.005 | 7 | 0.67 | 4200 | <0.05 | 0.0236 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0076 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 68.46 | 23.77 | 269 | N/S | N/S | N/S
2011-09-27 | 4.21 | 7.4 | 7.9 | 6 | 5 | N/S | <8 | <8 | 642 | 80 | 2.6 | <0.25 | 7.49 | 1.22 | N/S | N/S | N/S | N/S | <0.05 | 0.0205 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0063 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 56.01 | 20.39 | 224 | N/S | 2.7 | 5.9
2011-09-28 | 3.99 | 7.4 | 7 | 4 | 3 | N/S | <8 | <8 | 776 | 110 | 2.14 | <0.25 | 8.74 | 1 | N/S | N/S | N/S | N/S | <0.05 | 0.0256 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0063 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 68.11 | 25.49 | 275 | N/S | N/S | N/S
2011-09-29 | 3.67 | 7.3 | 8.2 | 5 | 4 | N/S | <8 | <8 | 820 | 114 | 1.69 | <0.25 | 10.67 | 1.3 | N/S | N/S | N/S | N/S | <0.05 | 0.0282 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0072 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 71.37 | 26.8 | 289 | N/S | N/S | N/S
2011-09-30 | 3.94 | 7.3 | 7.7 | N/S | N/S | N/S | <8 | <8 | 906 | 126 | 2.14 | <0.25 | 11.69 | 1.46 | N/S | N/S | N/S | N/S | <0.05 | 0.0294 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0079 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 75.05 | 28.61 | 305 | N/S | N/S | N/S
2011-10-01 | 2.83 | 7.2 | 7 | N/S | N/S | N/S | <8 | <8 | 974 | 122 | 2.28 | <0.25 | 14.36 | 1.61 | N/S | N/S | N/S | N/S | <0.05 | 0.0322 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0106 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 86.83 | 32.58 | 351 | N/S | N/S | N/S
2011-10-02 | 1.84 | 7.6 | 7.5 | 5 | 3 | N/S | <8 | <8 | 1006 | 130 | 2.4 | 0.27 | 18.37 | 2.47 | N/S | N/S | N/S | N/S | <0.05 | 0.0312 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 87.96 | 33.07 | 356 | N/S | N/S | N/S
2011-10-03 | 2.27 | 7.6 | 7.3 | 6 | 4 | <2 | <8 | <8 | 1049 | 160 | 2.12 | 0.25 | 20.1 | 2.77 | 0.005 | 9 | 0.86 | 1200 | <0.05 | 0.0306 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0086 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 86.95 | 32.64 | 352 | N/S | N/S | N/S
2011-10-04 | 1.78 | 7.4 | 7.2 | 5 | 3 | N/S | <8 | <8 | 1012 | 164 | 2.13 | <0.25 | 20.58 | 2.97 | N/S | N/S | N/S | N/S | <0.05 | 0.0285 | <0.001 | <0.01 | <0.02 | <0.2 | <0.2 | <0.03 | 0.0078 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 82.39 | 31.22 | 334 | N/S | <2.5 | 5.4
2011-10-05 | 1.8 | 7.4 | 7.7 | 6 | 3 | N/S | <8 | <8 | 980 | 142 | 2.29 | <0.25 | 23.2 | 3.29 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 76.39 | 28.93 | 310 | N/S | N/S | N/S
2011-10-06 | 1.86 | 7.4 | 7.4 | 4 | <2 | N/S | <8 | <8 | 1152 | 220 | 2.66 | <0.25 | 22.67 | 3.25 | N/S | N/S | N/S | N/S | <0.05 | 0.0318 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0096 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 97.25 | 32.19 | 375 | N/S | N/S | N/S
2011-10-07 | 1.75 | 7.4 | 7.7 | N/S | N/S | N/S | <8 | <8 | 1298 | 234 | 2.71 | <0.25 | 22.13 | 3.28 | N/S | N/S | N/S | N/S | <0.05 | 0.0367 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0093 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 113.29 | 35.78 | 430 | N/S | N/S | N/S
2011-10-08 | 1.82 | 7.5 | 6.9 | N/S | N/S | N/S | <8 | <8 | 1396 | 226 | 2.88 | 0.34 | 22.54 | 3.47 | N/S | N/S | N/S | N/S | <0.05 | 0.0379 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0121 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 115.65 | 36.86 | 441 | N/S | N/S | N/S
2011-10-09 | 1.76 | 7.4 | 6.9 | 7 | 5 | N/S | <8 | <8 | 1406 | 212 | 2.79 | 0.53 | 21.76 | 3.41 | N/S | N/S | N/S | N/S | <0.05 | 0.0352 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0136 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 105.88 | 35.64 | 411 | N/S | N/S | N/S
2011-10-10 | 1.77 | 7.5 | 6.3 | 6 | 4 | 2.4 | <8 | <8 | 1407 | 214 | 2.33 | 0.36 | 22.8 | 3.43 | 0.008 | 6 | 1.02 | 89000 | <0.05 | 0.0339 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.012 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 104.88 | 35.92 | 410 | N/S | N/S | N/S
2011-10-11 | 1.71 | 7.5 | 7.2 | 8 | 5 | N/S | <8 | <8 | 1440 | 260 | 2.51 | 0.27 | 22.07 | 3.19 | N/S | N/S | N/S | N/S | <0.05 | 0.0333 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0107 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 101.03 | 35.46 | 398 | N/S | <2.5 | 5.7
2011-10-12 | 1.64 | 7.5 | 6.5 | 7 | 5 | N/S | <8 | <8 | 1182 | 162 | 2.51 | <0.25 | 23.22 | 3.71 | N/S | N/S | N/S | N/S | <0.05 | 0.0271 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0088 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 81.79 | 29.66 | 326 | N/S | N/S | N/S
2011-10-13 | 2.39 | 7.4 | 6.4 | 9 | 6 | N/S | 8 | <8 | 900 | 150 | 2.13 | <0.25 | 20.6 | 3.36 | N/S | N/S | N/S | N/S | <0.05 | 0.0219 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0078 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 63.48 | 24.25 | 258 | N/S | N/S | N/S
2011-10-14 | 3.02 | 7.3 | 6.8 | N/S | N/S | N/S | <8 | <8 | 742 | 118 | 1.72 | <0.25 | 15.26 | 2.34 | N/S | N/S | N/S | N/S | <0.05 | 0.0214 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0081 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 61.21 | 24.12 | 252 | N/S | N/S | N/S
2011-10-15 | 2.09 | 7.4 | 7.4 | N/S | N/S | N/S | <8 | <8 | 824 | 130 | 1.93 | <0.25 | 17.27 | 2.47 | N/S | N/S | N/S | N/S | <0.05 | 0.0244 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0106 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 70.47 | 27.8 | 290 | N/S | N/S | N/S
2011-10-16 | 1.78 | 7.5 | 7 | 7 | 5 | N/S | <8 | <8 | 878 | 124 | 2.08 | <0.25 | 21.04 | 2.92 | N/S | N/S | N/S | N/S | <0.05 | 0.0251 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0118 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 72.45 | 28.06 | 296 | N/S | N/S | N/S
2011-10-17 | 1.84 | 7.5 | 7 | 7 | 5 | 2.2 | <8 | <8 | 894 | 142 | 2.11 | <0.25 | 21.13 | 2.94 | 0.006 | <6 | 0.92 | 10000 | <0.05 | 0.0257 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0113 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 71.84 | 27.16 | 291 | N/S | N/S | N/S
2011-10-18 | 1.84 | 7.5 | 7.1 | 9 | 6 | N/S | <8 | <8 | 886 | 176 | 2.01 | 0.3 | 21.27 | 2.65 | N/S | N/S | N/S | N/S | <0.05 | 0.0256 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0128 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 72.53 | 27.15 | 293 | N/S | 7 | 7
2011-10-19 | 1.88 | 7.4 | 7.4 | 15 | 8 | N/S | 31 | 26 | 912 | 194 | 3.49 | 0.25 | 22.62 | 3.23 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.01 | 0.0208 | 0.37 | N/S | <0.03 | 0.0405 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 71.95 | 26.76 | 290 | N/S | N/S | N/S
2011-10-20 | 3.35 | 7.4 | 7.5 | 8 | 5 | N/S | <8 | <8 | 672 | 102 | 1.37 | <0.25 | 13.89 | 1.62 | N/S | N/S | N/S | N/S | <0.05 | 0.0214 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0069 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 60.12 | 22.42 | 242 | N/S | N/S | N/S
2011-10-21 | 2.76 | 7.4 | 7.3 | N/S | N/S | N/S | 8 | <8 | 734 | 122 | 1.86 | 0.28 | 13.74 | 1.77 | N/S | N/S | N/S | N/S | <0.05 | 0.0239 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0087 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 68 | 25.65 | 275 | N/S | N/S | N/S
2011-10-22 | 2.63 | 7.4 | 7.9 | N/S | N/S | N/S | <8 | <8 | 1256 | 214 | 2.38 | 0.41 | 16.1 | 1.99 | N/S | N/S | N/S | N/S | <0.05 | 0.0423 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0145 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 110.47 | 33.98 | 416 | N/S | N/S | N/S
2011-10-23 | 1.98 | 7.5 | 8.1 | 5 | 3 | N/S | <8 | <8 | 1380 | 198 | 2.04 | 0.29 | 19.37 | 2.49 | N/S | N/S | N/S | N/S | <0.05 | 0.0413 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0104 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 108.02 | 34.7 | 413 | N/S | N/S | N/S
2011-10-24 | 2.44 | 7.4 | 7.6 | 4 | 2 | 2.2 | <8 | <8 | 1337 | 206 | 2.05 | <0.25 | 17.75 | 2.26 | 0.01 | <6 | 0.81 | 24000 | <0.05 | 0.0362 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0063 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 93.36 | 31.8 | 364 | N/S | N/S | N/S
2011-10-25 | 2.38 | 7.4 | 8.2 | 5 | 3 | N/S | <8 | <8 | 1246 | 156 | 2.03 | <0.25 | 18.69 | 2.22 | N/S | N/S | N/S | N/S | <0.05 | 0.0341 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0059 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 88.67 | 31.61 | 352 | N/S | <2.5 | 4.9
2011-10-26 | 2.39 | 7.4 | 7.1 | 3 | <2 | N/S | <8 | <8 | 1153 | 152 | 2.27 | <0.25 | 17.08 | 2.03 | N/S | N/S | N/S | N/S | <0.05 | 0.0318 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0053 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 83.88 | 30.78 | 336 | N/S | N/S | N/S
2011-10-27 | 2.27 | 7.4 | 7.3 | 4 | 3 | N/S | <8 | <8 | 1210 | 156 | 2.05 | <0.25 | 18.14 | 2.11 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0058 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 84.38 | 31.46 | 340 | N/S | N/S | N/S
2011-10-28 | 1.81 | 7.4 | 7 | N/S | N/S | N/S | <8 | <8 | 1217 | 160 | 2.34 | <0.25 | 18.85 | 2.39 | N/S | N/S | N/S | N/S | <0.05 | 0.0316 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.006 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 86.14 | 32.47 | 349 | N/S | N/S | N/S
2011-10-29 | 1.8 | 7.5 | 7 | N/S | N/S | N/S | <8 | <8 | 1168 | 144 | 2.22 | <0.25 | 20.45 | 2.53 | N/S | N/S | N/S | N/S | <0.05 | 0.0298 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0065 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 82.03 | 31.28 | 334 | N/S | N/S | N/S
2011-10-30 | 2.2 | 7.5 | 8.6 | 6 | 3 | N/S | <8 | <8 | 1149 | 148 | 2.74 | 0.8 | 19.79 | 2.57 | N/S | N/S | N/S | N/S | <0.05 | 0.0287 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0133 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 78.95 | 30.35 | 322 | N/S | N/S | N/S
2011-10-31 | 2.11 | 7.4 | 7 | 6 | 4 | 2.6 | <8 | <8 | 1080 | 156 | 2.25 | 0.33 | 17.73 | 2.27 | <0.005 | <6 | 1 | 10000 | <0.05 | 0.029 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0098 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 79.67 | 30.54 | 325 | N/S | N/S | N/S
2011-11-01 | 1.83 | 7.5 | 7.2 | 7 | 5 | N/S | <8 | <8 | 1114 | 164 | 2.46 | <0.25 | 20.46 | 2.55 | N/S | N/S | N/S | N/S | <0.05 | 0.0288 | <0.001 | <0.01 | <0.02 | <0.2 | <0.2 | <0.03 | 0.0075 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 83.76 | 31.99 | 341 | N/S | <2.5 | 5.9
2011-11-02 | 1.73 | 7.3 | 7.7 | 8 | 5 | N/S | <8 | <8 | 1132 | 156 | 2.58 | 0.27 | 20.67 | 2.73 | N/S | N/S | N/S | N/S | <0.05 | 0.0296 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0095 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 88.47 | 33.37 | 358 | N/S | N/S | N/S
2011-11-03 | 2.03 | 7.4 | 6.9 | 8 | 5 | N/S | <8 | <8 | 1090 | 150 | 2.5 | <0.25 | 21.26 | 2.68 | N/S | N/S | N/S | N/S | <0.05 | 0.028 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0077 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 83.47 | 31.47 | 338 | N/S | N/S | N/S
2011-11-04 | 2.36 | 7.3 | 7.1 | N/S | N/S | N/S | <8 | <8 | 996 | 164 | 0.82 | <0.25 | 18.03 | 2.27 | N/S | N/S | N/S | N/S | <0.05 | 0.0265 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0083 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 78.68 | 30.13 | 321 | N/S | N/S | N/S
2011-11-05 | 1.87 | 7.5 | 8.1 | N/S | N/S | N/S | <8 | <8 | 976 | 140 | 1.06 | <0.25 | 19.56 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.0258 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0085 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 78.2 | 29.71 | 318 | N/S | N/S | N/S
2011-11-06 | 2.04 | 7.5 | 8.2 | 7 | 5 | N/S | <8 | <8 | 956 | 122 | 1.78 | <0.25 | 20.87 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.0239 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0092 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 70.46 | 27.34 | 288 | N/S | N/S | N/S
2011-11-07 | 1.91 | 7.5 | 7.7 | 7 | 4 | 2.2 | <8 | <8 | 974 | 136 | 1.98 | 0.28 | 20.95 | 3.07 | <0.005 | 8 | 1.08 | 2400 | <0.05 | 0.0242 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0111 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 68.99 | 26.8 | 283 | N/S | N/S | N/S
2011-11-08 | 3.78 | 7.4 | 8.2 | 8 | 5 | N/S | <8 | <8 | 612 | 104 | 1.7 | <0.25 | 14.34 | 2.06 | N/S | N/S | N/S | N/S | <0.05 | 0.0191 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0062 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 54.58 | 20.9 | 222 | N/S | <2.5 | 6
2011-11-09 | 4.26 | 7.4 | 7.3 | 10 | 5 | N/S | 8 | <8 | 538 | 102 | 2.66 | <0.25 | 9.45 | 1.17 | N/S | N/S | N/S | N/S | <0.05 | 0.0208 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0059 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 57.58 | 22.22 | 235 | N/S | N/S | N/S
2011-11-10 | 4.26 | 7.3 | 7 | 11 | 6 | N/S | 13 | 10 | 752 | 128 | 2.13 | <0.25 | 10.49 | 1.05 | N/S | N/S | N/S | N/S | <0.05 | 0.0322 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0071 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 83.95 | 29.22 | 330 | N/S | N/S | N/S
2011-11-11 | 3.64 | 7.5 | 7.4 | N/S | N/S | N/S | 9 | <8 | 948 | 176 | 1.96 | <0.25 | 11.36 | 1.31 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.008 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 96.58 | 33.7 | 380 | N/S | N/S | N/S
2011-11-12 | 2.97 | 7.4 | 8.6 | N/S | N/S | N/S | <8 | <8 | 1131 | 184 | 2.76 | <0.25 | 14.33 | 1.6 | N/S | N/S | N/S | N/S | <0.05 | 0.0391 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0112 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 99.06 | 35.98 | 396 | N/S | N/S | N/S
2011-11-13 | 2.41 | 7.5 | 7.1 | 8 | 4 | N/S | <8 | <8 | 1108 | 136 | 2.89 | <0.25 | 15.2 | 1.82 | N/S | N/S | N/S | N/S | <0.05 | 0.0367 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0123 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 94.79 | 35.35 | 382 | N/S | N/S | N/S
2011-11-14 | 2 | 7.5 | 7 | 6 | 3 | 2 | <8 | <8 | 1114 | 150 | 2 | <0.25 | 16.4 | 1.94 | <0.005 | <6 | 0.8 | 14000 | <0.05 | 0.0341 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0081 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 91.22 | 34.32 | 369 | N/S | N/S | N/S
2011-11-15 | 1.83 | 7.6 | 8.7 | 7 | 4 | N/S | <8 | <8 | 1174 | 174 | 1.86 | 0.26 | 18.02 | 2.16 | N/S | N/S | N/S | N/S | <0.05 | 0.0355 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.008 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 93.75 | 34.71 | 377 | N/S | <2.5 | 5.2
2011-11-16 | 1.85 | 7.5 | 7.8 | 7 | 5 | N/S | <8 | <8 | 1264 | 172 | 2.58 | <0.25 | 21.19 | 2.57 | N/S | N/S | N/S | N/S | <0.05 | 0.0358 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0077 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 96.76 | 35.89 | 389 | N/S | N/S | N/S
2011-11-17 | 1.83 | 7.5 | 8.3 | 7 | 4 | N/S | <8 | <8 | 1177 | 106 | 2.17 | <0.25 | 20.49 | 2.47 | N/S | N/S | N/S | N/S | <0.05 | 0.0343 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0073 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 95.26 | 35.35 | 383 | N/S | N/S | N/S
2011-11-18 | 1.86 | 7.5 | 8.4 | N/S | N/S | N/S | <8 | <8 | 1171 | 148 | 1.82 | <0.25 | 20.69 | 2.77 | N/S | N/S | N/S | N/S | <0.05 | 0.0329 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0064 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 89.22 | 33.4 | 360 | N/S | N/S | N/S
2011-11-19 | 1.74 | 7.4 | 8.2 | N/S | N/S | N/S | <8 | <8 | 1169 | 174 | 1.85 | <0.25 | 20.62 | 2.76 | N/S | N/S | N/S | N/S | <0.05 | 0.0328 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0066 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 92.05 | 34.37 | 371 | N/S | N/S | N/S
2011-11-20 | 2.16 | 7.4 | 8.3 | 9 | 5 | N/S | <8 | <8 | 1144 | 172 | 2.29 | 0.98 | 19.24 | 2.64 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0112 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 89.5 | 33.27 | 361 | N/S | N/S | N/S
2011-11-21 | 1.79 | 7.5 | 7.4 | 6 | 4 | 2 | <8 | <8 | 1118 | 166 | 2.05 | 0.28 | 19.34 | 2.44 | <0.005 | 6 | 1 | 6700 | <0.05 | 0.0307 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.009 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 86.76 | 32.05 | 349 | N/S | N/S | N/S
2011-11-22 | 1.95 | 7.4 | 7.7 | 7 | 4 | N/S | <8 | <8 | 1003 | 124 | 1.86 | <0.25 | 20.17 | 2.64 | N/S | N/S | N/S | N/S | <0.05 | 0.0281 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0068 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 79.06 | 29.88 | 320 | N/S | <2.5 | 6
2011-11-23 | 2.41 | 7.4 | 8.3 | 6 | 4 | N/S | <8 | <8 | 1067 | 194 | 2.32 | <0.25 | 16.57 | 2.24 | N/S | N/S | N/S | N/S | <0.05 | 0.0323 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0068 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 92.37 | 31.83 | 362 | N/S | N/S | N/S
2011-11-24 | 2.27 | 7.4 | 8.4 | 7 | 5 | N/S | <8 | <8 | 1105 | 168 | 1.95 | <0.25 | 17.89 | 2.31 | N/S | N/S | N/S | N/S | <0.05 | 0.0346 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.009 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 97.11 | 33.13 | 379 | N/S | N/S | N/S
2011-11-25 | 1.86 | 7.5 | 7.4 | N/S | N/S | N/S | <8 | <8 | 1170 | 188 | 3.71 | <0.25 | 17.7 | 2.52 | N/S | N/S | N/S | N/S | <0.05 | 0.0344 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0097 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 94.44 | 32.86 | 371 | N/S | N/S | N/S
2011-11-26 | 2.39 | 7.4 | 7.7 | N/S | N/S | N/S | <8 | <8 | 1077 | 166 | 2.9 | <0.25 | 18.75 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.0318 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0091 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 85.13 | 30.48 | 338 | N/S | N/S | N/S
2011-11-27 | 4.34 | 7.3 | 8.2 | 5 | 3 | N/S | <8 | <8 | 662 | 112 | 2.88 | <0.25 | 10.27 | 1.38 | N/S | N/S | N/S | N/S | <0.05 | 0.0238 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 61.04 | 22.8 | 246 | N/S | N/S | N/S
2011-11-28 | 4.19 | 7.4 | 8 | 7 | 4 | 2 | 11 | 8 | 768 | 112 | 1.93 | <0.25 | 11.25 | 1.19 | <0.005 | 6 | 0.56 | 13000 | <0.05 | 0.028 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0071 | N/S | <0.008 | 0.007 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 71.64 | 27.7 | 293 | N/S | N/S | N/S
2011-11-29 | 3.72 | 7.4 | 7.6 | 7 | 4 | N/S | 8 | <8 | 866 | 132 | 2.12 | <0.25 | 12.47 | 1.35 | N/S | N/S | N/S | N/S | <0.05 | 0.0337 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0081 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 80.97 | 31.25 | 331 | N/S | <2.5 | 5.3
2011-11-30 | 2.98 | 7.4 | 8.3 | 7 | 4 | N/S | 5 | 5 | 958 | 146 | 2.18 | <0.25 | 16.13 | 1.76 | N/S | N/S | N/S | N/S | <0.05 | 0.0325 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0079 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 86.57 | 32.73 | 351 | N/S | N/S | N/S
2011-12-01 | 2.17 | 7.6 | 6.8 | 7 | 5 | N/S | <8 | <8 | 1038 | 154 | 2.23 | <0.25 | 18.28 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.0325 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0064 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.12 | 34.23 | 366 | N/S | N/S | N/S
2011-12-02 | 1.99 | 7.5 | 8.2 | N/S | N/S | N/S | <8 | <8 | 1111 | 168 | 2.51 | <0.25 | 18.51 | 2.41 | N/S | N/S | N/S | N/S | <0.05 | 0.0314 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0068 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 87.04 | 32.98 | 353 | N/S | N/S | N/S
2011-12-03 | 1.99 | 7.5 | 8.6 | N/S | N/S | N/S | <8 | <8 | 1122 | 166 | 1.84 | <0.25 | 18.41 | 2.39 | N/S | N/S | N/S | N/S | <0.05 | 0.0311 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 87.51 | 33.09 | 355 | N/S | N/S | N/S
2011-12-04 | 2.35 | 7.4 | 8.6 | 11 | 10 | N/S | 27 | 22 | 1000 | 160 | 3.67 | <0.25 | 16.36 | 2.54 | N/S | N/S | N/S | N/S | <0.05 | 0.0341 | <0.001 | <0.01 | <0.02 | 0.31 | N/S | <0.03 | 0.03 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 77.89 | 29.72 | 317 | N/S | N/S | N/S
2011-12-05 | 2.96 | 7.5 | 8.2 | 9 | 6 | 2 | <8 | <8 | 948 | 150 | 1.87 | <0.25 | 16.39 | 2.1 | <0.005 | <6 | 0.79 | 2000 | <0.05 | 0.0304 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0114 | N/S | <0.008 | 0.007 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 82.52 | 32.55 | 340 | N/S | N/S | N/S
2011-12-06 | 2.41 | 7.4 | 8.3 | 9 | 5 | N/S | <8 | <8 | 1006 | 162 | 1.75 | <0.25 | 17.63 | 2.13 | N/S | N/S | N/S | N/S | <0.05 | 0.0306 | <0.001 | <0.01 | <0.02 | <0.2 | <0.2 | <0.03 | 0.0084 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 84.74 | 33.13 | 348 | N/S | <2.5 | 4.9
2011-12-07 | 1.97 | 7.5 | 8.4 | 10 | 6 | N/S | <8 | <8 | 1063 | 158 | 2.51 | <0.25 | 18.88 | 2.61 | N/S | N/S | N/S | N/S | <0.05 | 0.0298 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0061 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 83.35 | 32.57 | 342 | N/S | N/S | N/S
2011-12-08 | 2.1 | 7.5 | 8.8 | 10 | 7 | N/S | <8 | <8 | 1064 | 104 | 2.47 | <0.25 | 19.7 | 2.76 | N/S | N/S | N/S | N/S | <0.05 | 0.0294 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0084 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 81.2 | 31.78 | 334 | N/S | N/S | N/S
2011-12-09 | 2.02 | 7.5 | 8.5 | N/S | N/S | N/S | 8 | <8 | 1064 | 172 | 2.27 | <0.25 | 21.2 | 2.81 | N/S | N/S | N/S | N/S | <0.05 | 0.028 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0073 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 77.16 | 30.5 | 318 | N/S | N/S | N/S
2011-12-10 | 1.99 | 7.5 | 8 | N/S | N/S | N/S | <8 | <8 | 952 | 160 | 1.97 | <0.25 | 19.83 | 2.77 | N/S | N/S | N/S | N/S | <0.05 | 0.0257 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0074 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 72.75 | 29.06 | 301 | N/S | N/S | N/S
2011-12-11 | 1.72 | 7.6 | 8.7 | 7 | 4 | N/S | <8 | <8 | 956 | 126 | 2.36 | <0.25 | 19.55 | 2.79 | N/S | N/S | N/S | N/S | <0.05 | 0.0255 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0069 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 73.06 | 29.41 | 304 | N/S | N/S | N/S
2011-12-12 | 1.93 | 7.4 | 8 | 7 | 4 | 3.1 | <8 | <8 | 1007 | 138 | 2.66 | 0.26 | 21.5 | 3.01 | 0.005 | <6 | 1.04 | 2300 | <0.05 | 0.0248 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0082 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 72.03 | 28.7 | 298 | N/S | N/S | N/S
2011-12-13 | 1.72 | 7.5 | 7.7 | 5 | 3 | N/S | <8 | <8 | 984 | 158 | 2.16 | <0.25 | 21.97 | 2.97 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0076 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 74.53 | 29.17 | 306 | N/S | <2.5 | 6
2011-12-14 | 3.63 | 7.6 | 7.7 | 9 | 6 | N/S | <8 | <8 | 744 | 72 | 1.66 | <0.25 | 14.05 | 2 | N/S | N/S | N/S | N/S | <0.05 | 0.0214 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0065 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 60.48 | 23.23 | 247 | N/S | N/S | N/S
2011-12-15 | 4.31 | 7.3 | 8.1 | 10 | 6 | N/S | <8 | <8 | 584 | 112 | 1.64 | <0.25 | 8.96 | 1.08 | N/S | N/S | N/S | N/S | <0.05 | 0.0211 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0056 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 59.64 | 23.5 | 246 | N/S | N/S | N/S
2011-12-16 | 4.24 | 7.5 | 7.9 | N/S | N/S | N/S | <8 | <8 | 826 | 192 | 2.48 | <0.25 | 10.63 | 1.44 | N/S | N/S | N/S | N/S | <0.05 | 0.0325 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0069 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 84.41 | 30.39 | 336 | N/S | N/S | N/S
2011-12-17 | 3.79 | 7.3 | 7.7 | N/S | N/S | N/S | 8 | <8 | 1083 | 216 | 3.29 | 0.78 | 12.43 | 1.68 | N/S | N/S | N/S | N/S | <0.05 | 0.0383 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0133 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 95.66 | 33.28 | 376 | N/S | N/S | N/S
2011-12-18 | 2.78 | 7.4 | 8 | 11 | 5 | N/S | <8 | <8 | 1147 | 156 | 4.34 | 1.77 | 13.36 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.0369 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0159 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 92.89 | 33.84 | 371 | N/S | N/S | N/S
2011-12-19 | 2.43 | 7.5 | 7.9 | 9 | 5 | 3.1 | <8 | <8 | 1261 | 192 | 2.65 | <0.25 | 17.23 | 2.28 | <0.005 | 8 | 0.76 | 1400 | <0.05 | 0.0355 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0079 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.94 | 34.02 | 367 | N/S | N/S | N/S
2011-12-20 | 2.2 | 7.5 | 7.8 | 8 | 4 | N/S | 9 | <8 | 1261 | 188 | 2.65 | <0.25 | 19.09 | 2.65 | N/S | N/S | N/S | N/S | <0.05 | 0.0362 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.007 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 94 | 35.39 | 380 | N/S | <2.5 | 5
2011-12-21 | 2.17 | 7.5 | 8.2 | 7 | 4 | N/S | <8 | <8 | 1291 | 200 | 3.87 | <0.25 | 19.97 | 2.74 | N/S | N/S | N/S | N/S | <0.05 | 0.0338 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0069 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 89.79 | 34.07 | 365 | N/S | N/S | N/S
2011-12-22 | 2.15 | 7.5 | 8.1 | 6 | 4 | N/S | <8 | <8 | 1220 | 176 | 2.47 | <0.25 | 21.26 | 2.65 | N/S | N/S | N/S | N/S | <0.05 | 0.0341 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0069 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 91.13 | 35.13 | 372 | N/S | N/S | N/S
2011-12-23 | 2.29 | 7.5 | 8.3 | N/S | N/S | N/S | 68 | 44 | 1171 | 174 | 2.91 | <0.25 | 19.74 | 2.67 | N/S | N/S | N/S | N/S | <0.05 | 0.0329 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.009 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 88.38 | 34.44 | 362 | N/S | N/S | N/S
2011-12-24 | 2.24 | 7.5 | 7.4 | N/S | N/S | N/S | <8 | <8 | 1127 | 154 | 4.33 | 1.85 | 17.15 | 2.43 | N/S | N/S | N/S | N/S | <0.05 | 0.0319 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0136 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 85.5 | 33.14 | 350 | N/S | N/S | N/S
2011-12-25 | 1.99 | 7.4 | 6.5 | 8 | 5 | N/S | <8 | <8 | 1085 | 142 | 3.56 | 1.01 | 18.54 | 2.64 | N/S | N/S | N/S | N/S | <0.05 | 0.0306 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0135 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 80.04 | 31.61 | 330 | N/S | N/S | N/S
2011-12-26 | 2.01 | 7.5 | 7 | 9 | 5 | <2 | <8 | <8 | 1110 | 162 | 3.46 | 0.95 | 20.88 | 3.01 | 0.007 | 10 | 0.9 | N/S | <0.05 | 0.0316 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0153 | N/S | <0.008 | 0.006 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 84.12 | 33.29 | 347 | N/S | N/S | N/S
2011-12-27 | 2.23 | 7.4 | 6.2 | 9 | 5 | N/S | 8 | 8 | 1003 | 152 | 2.76 | <0.25 | 18.77 | 2.67 | N/S | N/S | N/S | 7700 | <0.05 | 0.0271 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0107 | <0.2 | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | <6 | 74.16 | 29.67 | 307 | N/S | <2.5 | 5.8
2011-12-28 | 2.44 | 7.4 | 8.4 | 9 | 6 | N/S | 8 | <8 | 944 | 130 | 2.34 | <0.25 | 18.19 | 2.44 | N/S | N/S | N/S | N/S | <0.05 | 0.0272 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0083 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 73.1 | 30.4 | 308 | N/S | N/S | N/S
2011-12-29 | 2.22 | 7.6 | 7.2 | 10 | 6 | N/S | 8 | <8 | 916 | 152 | 3.31 | 0.44 | 17.98 | 2.51 | N/S | N/S | N/S | N/S | <0.05 | 0.0266 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0162 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 69.24 | 29.08 | 293 | N/S | N/S | N/S
2011-12-30 | 2.69 | 7.5 | 7.2 | N/S | N/S | N/S | 10 | 8 | 1053 | 206 | 3.02 | <0.25 | 16.27 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.0336 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.0184 | N/S | <0.008 | <0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.08 | 32.33 | 358 | N/S | N/S | N/S
2011-12-31 | 3.22 | 7.4 | 8.1 | N/S | N/S | N/S | 10 | 8 | 1038 | 200 | 2.73 | <0.25 | 14.08 | 1.68 | N/S | N/S | N/S | N/S | <0.05 | 0.0345 | <0.001 | <0.01 | <0.02 | <0.2 | N/S | <0.03 | 0.012 | N/S | <0.008 | 0.005 | <0.004 | <0.06 | <0.05 | <0.001 | <0.02 | N/S | 90.37 | 33.72 | 364 | N/S | N/S | N/S
Reporting Limit (RL) |  |  |  | 2 | 2 | 2 | 8 | 8 | 90 |  | 0.45 | 0.25 | 0.15 | 0.15 | 0.005 | 6 | 0.1 | 10 | 0.04 | 0.02 | 0.001 | 0.002 | 0.003 | 0.05 | 0.01 | 0.02 | 0.002 | 0.2 | 0.003 | 0.005 | 0.003 | 0.01 | 0.03 | 0.002 | 0.1 | 6 | 0.3 | 0.2 |  | 0.2 | 0.5* | 1
Reporting Limit (RL) From August 17, 2011 |  |  |  | 2 | 2 | 2 | 8 | 8 | 90 |  | 0.45 | 0.25 | 0.15 | 0.15 | 0.005 | 6 | 0.1 | 10 | 0.05 | 0.004 | 0.001 | 0.01 | 0.02 | 0.2 | 0.2 | 0.03 | 0.003 | 0.2 | 0.008 | 0.005 | 0.004 | 0.06 | 0.05 | 0.001 | 0.02 | 6 | 0.3 | 0.3 |  | 0.2 | 0.5* | 1
Observations | 365 | 365 | 365 | 259 | 259 | 52 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 52 | 52 | 52 | 52 | 365 | 365 | 365 | 365 | 365 | 365 | 12 | 365 | 365 | 52 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 52 | 365 | 365 | 365 | 0 | 52 | 52
Minimum | 1.49 | 6.3 | 4.3 | <2 | <2 | <2 | <8 | <8 | 538 | 72 | <0.45 | <0.25 | 7.4 | 0.77 | <0.005 | <6 | 0.45 | 1200 | <0.04 | 0.0127 | <0.001 | <0.002 | <0.003 | <0.05 | <0.01 | <0.02 | 0.0015 | <0.2 | <0.003 | <0.005 | <0.003 | 0.02 | <0.03 | <0.001 | <0.02 | <6 | 54.58 | 20.39 | 222 |  | <0.5 | 3.2
Mean | 2.56 | 7.3 | 7.8 | <7 | <4 | <2 | <8 | <8 | 1149 | 184 | <2.60 | <0.25 | 16.95 | 2.25 | <0.005 | <6 | 0.82 | 21719 | <0.04 | 0.0319 | <0.001 | <0.005 | <0.012 | <0.13 | <0.09 | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | <0.003 | 0.05 | <0.04 | <0.002 | <0.07 | <6 | 88.58 | 33.15 | 358 |  | <2.7 | 5.6
Maximum | 4.51 | 7.8 | 10.6 | 15 | 10 | 4 | 68 | 44 | 2263 | 426 | 5.11 | 1.85 | 25.18 | 4 | 0.01 | 17 | 1.09 | 260000 | <0.05 | 0.0614 | 0.0014 | <0.010 | 0.0857 | 1.48 | <0.20 | <0.03 | 0.067 | <0.2 | 0.0101 | 0.009 | <0.004 | 0.134 | <0.05 | <0.002 | <0.10 | <6 | 125.35 | 43.41 | 491 |  | 9.1 | 7.7
Std Dev | 0.86 | 0.2 | 1 | 2 | 1 | 0.5 | 5 | 3 | 262 | 55 | 0.84 | 0.26 | 4.38 | 0.74 | 0.001 | 3 | 0.17 | 40939 | 0 | 0.0056 | 0.0005 | 0.0038 | 0.0069 | 0.1 | 0.08 | 0 | 0.0064 | 0 | 0.0028 | 0.002 | 0.0016 | 0.014 | 0.01 | 0 | 0.04 | 1 | 13.7 | 4.15 | 50 |  | 1.8 | 0.9
Note: Except for soluble Fe, soluble metals are no longer being analyzed.
* LL Hg: Based on the sample matrix some samples need to be diluted x2, x5 and x10. The reporting limit
of 0.5 ng/L for LL Hg will then change by the same factor resulting in reporting limits of 1.0, 2.5, and 5.0 ng/L respectively.
January 10 and 17, 2011 Phenol: Sample/aliquot holding time exceeded.
January 27, 2011 BOD5, CBOD5: 6 day BOD
February 22, 2011 BOD5, CBOD5 T/X: Unrepresentative sample aliquout used for BOD5.
April 7, 2011 BOD5, CBOD5: Batch failed QA standard; analysis exempt from rerun.
April 13-16 and 20-26, 2011 Se: LOQ not within acceptance limits.
April 17-30, 2011 Cu: LOQ not within acceptance limits.
April 17-19 and 24-26 Ca: LOQ not within acceptance limits.
May 1-10, 21-24 and 29-31, 2011 Se and Cu: LOQ not within acceptance limits.
May 1-3 and 11-13, 2011 Ca: LOQ not within acceptance limits.
May 5, 2011 NH3_N: One reagent was expired; no QA failures associated with qualified results.
May 7-10 and 14, 2011 Cd: LOQ not within acceptance limits.
May 9, 2011 FOG: Lemont Raw and Lemont Outfall look like the labels were swapped at collection.
May 11-13, 2011 Mn: LOQ not within acceptance limits.
May 14-17, 2011 Cd, Cu, Cr, Fe, Ni, Pb, Ag, Mn, As, Se, Ba, Sb, Be, Tl Ca, Mg, and Zn: LOQ not within acceptance limits.
May 29-31, 2011 Ni: LOQ not within acceptance limits.
June 5-26 and 30, 2011 Cu, and Se: LOQ not within acceptance limits.
June 6, and 12-14, 2011 Fe: LOQ not within acceptance limits.
June 12-14, 2011 Cd: LOQ not within acceptance limits.
June 15-18, 2011 As: LOQ not within acceptance limits.
June 28, 2011 BOD5, CBOD5: Batch failed QA standard; analysis exempt from rerun.
June 30, 2011 Zn: LOQ not within acceptance limits.
July 1-3 and 7-10, 2011 Cu, Se, and Zn: LOQ not within acceptance limits.
July 4-6, 2011 Cu: LOQ not within acceptance limits.
July 11-14 Cd, Cu, Fe, Mn, Se, and Zn: LOQ not within acceptance limits.
July 15-17, 2011 Cd, Cu, and Se: LOQ not within acceptance limits.
July 24-26, 2011 Se and Ca: LOQ not within acceptance limits.
August 3-6, 2011 Cu, Se, and Ca: LOQ not within acceptance limits.
September 15 and 22, 2011 BOD5, CBOD5: Batch failed QA standard; analysis exempt from rerun.
November 30, 2011 ZN: Method blank criteria exceeded; insufficient volume for reanalysis.
December 1-4, 2011 ZN: Method blank criteria exceeded; insufficient volume for reanalysis.
December 6, 12, and 15, 2011 BOD5, CBOD5: Batch failed QA standard analysis exempt from rerun.

## Lemont Outfall 2012
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg Sol | *Low Level Hg | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | ng/L | mg/L
2012-01-01 | 2.55 | 7.3 | 7.3 | 10 | 5 | N/S | 6 | 6 | 1088 | 190 | 2 | 0.1 | 15.2 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-02 | 2.51 | 7.4 | 8.5 | 11 | 6 | <5 | 6 | 4 | 1152 | 210 | 3 | 0.6 | 16.16 | 2.3 | 0.005 | 6 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-03 | 2.12 | 7.4 | 8.6 | 10 | 5 | N/S | 6 | 5 | 1205 | 208 | 3 | 0.2 | 18.38 | 2.4 | N/S | N/S | N/S | 7600 | <0.05 | 0.035 | <0.001 | <0.005 | 0.008 | 0.1 | <0.1 | <0.02 | 0.013 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 92 | 36 | 380 | N/S | <2.5 | 6
2012-01-04 | 2.08 | 7.5 | 7.3 | 8 | 4 | N/S | 4 | 2 | 1313 | 196 | 3 | 0.2 | 18.52 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-05 | 2.06 | 7.3 | 7.1 | 8 | 5 | N/S | 6 | 2 | 1240 | 188 | 3 | 0.2 | 19.85 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-06 | 1.94 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 3 | 1253 | 218 | 3 | 0.2 | 20.53 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-07 | 1.72 | 7.3 | 6.3 | N/S | N/S | N/S | 6 | 3 | 1257 | 206 | 3 | 0.2 | 22.24 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-08 | 1.85 | 7.3 | 8.5 | 11 | 7 | N/S | 8 | 5 | 1201 | 168 | 3 | 0.2 | 22.15 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-09 | 2.06 | 7.4 | 8.7 | 11 | 7 | <5 | 8 | 5 | 1153 | 188 | 2 | 0.2 | 23.14 | 2.7 | 0.006 | 10 | 1.2 | 9300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-10 | 1.97 | 7.4 | 8 | 11 | 6 | N/S | 8 | 8 | 1134 | 168 | 2 | 0.2 | 22.55 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 85 | 34 | 353 | N/S | <2.5 | 6
2012-01-11 | 1.72 | 7.4 | 7.2 | 10 | 5 | N/S | 9 | 5 | 1069 | 172 | 3 | 0.2 | 22.59 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-12 | 1.82 | 7.6 | 7.1 | 10 | 6 | N/S | 8 | 8 | 1032 | 138 | 3 | 0.2 | 24.28 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-13 | 1.85 | 7.6 | 7.1 | N/S | N/S | N/S | 7 | 5 | 1453 | 204 | 3 | 0.2 | 22.91 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-14 | 1.85 | 7.6 | 8.9 | N/S | N/S | N/S | 12 | 9 | 1419 | 184 | 3 | 0.3 | 22.1 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-15 | 1.75 | 7.5 | 8.4 | 7 | 5 | N/S | 6 | 6 | 1186 | 152 | 3 | 0.3 | 22.55 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-16 | 1.93 | 7.5 | 7.7 | 7 | 4 | <5 | 5 | 4 | 1159 | 150 | 3 | 0.2 | 21.2 | 2.3 | 0.005 | 7 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-17 | 3.04 | 7.5 | 8 | 7 | 5 | N/S | 4 | 3 | 1663 | 224 | 3 | 0.2 | 16.16 | 1.8 | N/S | N/S | N/S | 8100 | <0.05 | 0.04 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | <0.005 | 0.002 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 97 | 36 | 391 | N/S | <0.5 | 5
2012-01-18 | 2.64 | 7.5 | 9.3 | 6 | 4 | N/S | 6 | 4 | 1493 | 214 | 3 | 0.2 | 14.94 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-19 | 2.29 | 7.6 | 8.4 | 7 | 5 | N/S | 8 | 4 | 1414 | 262 | 3 | 0.2 | 18.54 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-20 | 1.93 | 7.7 | 7.2 | N/S | N/S | N/S | 7 | 6 | 1262 | 244 | 2 | 0.2 | 19.27 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-21 | 2.09 | 7.6 | 8.2 | N/S | N/S | N/S | 9 | 6 | 1324 | 228 | 2 | 0.5 | 20.63 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-22 | 2.23 | 7.5 | 7.5 | 9 | 5 | N/S | 7 | 6 | 1632 | 274 | 2 | 0.2 | 20.71 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-23 | 3.98 | 7.3 | 7.9 | 8 | 5 | <5 | 8 | 6 | 1354 | 196 | 3 | 0.1 | 10.52 | 1.3 | 0.008 | 5 | 0.4 | 1800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-24 | 4.14 | 7.4 | 9.6 | 6 | 4 | N/S | 6 | 6 | 1250 | 180 | 2 | 0.1 | 9.08 | 0.8 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | <0.005 | 0.002 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 86 | 33 | 351 | N/S | <2.5 | 4
2012-01-25 | 4.21 | 7.4 | 9 | 6 | 5 | N/S | 9 | 8 | 1368 | 188 | 2 | 0.1 | 11.69 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-26 | 2.83 | 7.5 | 8.5 | 5 | 4 | N/S | 4 | 2 | 1237 | 208 | 2 | 0.1 | 13.75 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-27 | 2.92 | 7.4 | 8.8 | N/S | N/S | N/S | 7 | 4 | 1218 | 196 | 2 | 0.1 | 16.28 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-28 | 3.05 | 7.4 | 8.6 | N/S | N/S | N/S | 6 | 6 | 1467 | 186 | 3 | 0.1 | 16.12 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-29 | 2.89 | 7.5 | 8.5 | 8 | 6 | N/S | 6 | 5 | 1426 | 162 | 2 | 0.4 | 16.29 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-30 | 2.48 | 7.5 | 8.4 | 6 | 5 | <5 | 6 | 4 | 1348 | 136 | 3 | 0.2 | 17.87 | 1.9 | 0.006 | 8 | 0.7 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-01-31 | 2.52 | 7.5 | 8.8 | 5 | 6 | N/S | 8 | 4 | 1416 | 192 | 2 | 0.2 | 17.03 | 2 | N/S | N/S | N/S | N/S | <0.05 | 0.046 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | 0.007 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 105 | 41 | 433 | N/S | <2.5 | 5
2012-02-01 | 2.54 | 7.5 | 7.7 | 3 | 3 | N/S | 7 | 5 | 1418 | 170 | 2 | 0.2 | 17.71 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-02 | 2.77 | 7.6 | 8.6 | 8 | 4 | N/S | 7 | 4 | 1423 | 228 | 3 | 0.2 | 17.72 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-03 | 2.63 | 7.4 | 7.5 | N/S | N/S | N/S | 8 | 6 | 1317 | 230 | 4 | 0.2 | 17.51 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-04 | 2.55 | 7.3 | 10 | N/S | N/S | N/S | 8 | 5 | 1379 | 234 | 3 | 0.1 | 16.12 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-05 | 2.87 | 7.4 | 8 | 8 | 5 | N/S | 7 | 6 | 1300 | 200 | 3 | 0.7 | 14.82 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-06 | 2.85 | 7.4 | 7.6 | 9 | 4 | <5 | 6 | 6 | 1252 | 180 | 4 | 1.4 | 13.9 | 1.7 | 0.007 | 6 | 0.7 | 98000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-07 | 2.54 | 7.5 | 8 | 4 | 3 | N/S | 3 | 2 | 1221 | 160 | 2 | 0.2 | 16.12 | 1.7 | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.006 | 0.1 | <0.1 | <0.02 | 0.011 | <0.2 | <0.005 | 0.006 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 98 | 38 | 402 | N/S | <2.5 | 5
2012-02-08 | 2.48 | 7.6 | 8.6 | 5 | 4 | N/S | 4 | 2 | 1221 | 170 | 3 | 0.2 | 18.11 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-09 | 2.54 | 7.6 | 8.7 | 4 | 4 | N/S | 5 | 5 | 1234 | 200 | 2 | 0.2 | 19.43 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-10 | 2.28 | 7.4 | 8.8 | N/S | N/S | N/S | 5 | 2 | 1116 | 176 | 3 | 0.2 | 20.25 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-11 | 2.14 | 7.5 | 9.3 | N/S | N/S | N/S | 6 | 2 | 1208 | 196 | 3 | 0.3 | 20.78 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-12 | 2.11 | 7.4 | 9.3 | 10 | 6 | N/S | 13 | 10 | 1271 | 214 | 5 | 0.6 | 20.1 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-13 | 2.01 | 7.4 | 7.8 | 15 | 8 | <5 | 13 | 10 | 1241 | 212 | 4 | 0.7 | 21.36 | 2.9 | 0.005 | 11 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-14 | 1.87 | 7.4 | 8.1 | 11 | 9 | N/S | 10 | 8 | 1250 | 178 | 3 | 0.2 | 20.88 | 2.6 | N/S | N/S | N/S | 350000 | <0.05 | 0.035 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 89 | 35 | 365 | N/S | <2.5 | 7
2012-02-15 | 1.92 | 7.4 | 7 | 11 | 8 | N/S | 6 | 6 | 1359 | 206 | 3 | 0.3 | 21.22 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-16 | 2.65 | 7.3 | 7.4 | 10 | 6 | N/S | 10 | 10 | 1420 | 192 | 2 | 0.2 | 17.49 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-17 | 2.38 | 7.5 | 7.5 | N/S | N/S | N/S | 10 | 10 | 1424 | 218 | 3 | 0.1 | 17.83 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-18 | 2.15 | 7.4 | 7.8 | N/S | N/S | N/S | 10 | 8 | 1321 | 202 | 3 | 0.2 | 18.28 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-19 | 2.12 | 7.4 | 9.8 | 11 | 7 | N/S | 9 | 9 | 1227 | 180 | 3 | 0.5 | 18.98 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-20 | 2.01 | 7.4 | 7.5 | 11 | 8 | <5 | 10 | 7 | 1172 | 142 | 4 | 0.4 | 19.23 | 2.5 | 0.007 | 7 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-21 | 2.12 | 7.4 | 7.5 | 10 | 7 | N/S | 9 | 8 | 1277 | 216 | 3 | 0.3 | 18.26 | 2.3 | N/S | N/S | N/S | 9500 | <0.05 | 0.041 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 98 | 38 | 402 | N/S | <2.5 | 7
2012-02-22 | 2.1 | 7.5 | 8.6 | 10 | 5 | N/S | 7 | 5 | 1492 | 266 | 4 | 0.3 | 18.49 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-23 | 1.98 | 7.5 | 8.3 | 9 | 6 | N/S | 10 | 8 | 1362 | 244 | 3 | 0.3 | 20.56 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-24 | 2.54 | 7.4 | 7.6 | N/S | N/S | N/S | 10 | 8 | 1631 | 222 | 3 | 0.2 | 18.05 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-25 | 2.65 | 7.5 | 9.2 | N/S | N/S | N/S | 11 | 8 | 1579 | 194 | 3 | 0.2 | 16.84 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-26 | 2.47 | 7.4 | 9.3 | 13 | 7 | N/S | 12 | 10 | 1349 | 164 | 4 | 0.6 | 17.23 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-27 | 2.35 | 7.5 | 7.9 | 10 | 6 | <5 | 8 | 8 | 1299 | 212 | 4 | 0.7 | 17.62 | 2.5 | 0.006 | 5 | 0.8 | 8200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-02-28 | 2.06 | 7.5 | 8.7 | 14 | 6 | N/S | 11 | 10 | 1156 | 168 | 4 | 0.3 | 18.01 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | <0.005 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 89 | 36 | 370 | N/S | <2.5 | 8
2012-02-29 | 2.49 | 7.4 | 6.9 | 13 | 7 | N/S | 9 | 7 | 1265 | 192 | 4 | 0.3 | 16.16 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-01 | 3.11 | 7.6 | 8.4 | 16 | 8 | N/S | 12 | 10 | 1229 | 164 | 4 | 0.2 | 15.67 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-02 | 2.82 | 7.4 | 6.5 | N/S | N/S | N/S | 13 | 11 | 1158 | 156 | 3 | 0.2 | 15.81 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-03 | 2.75 | 7.6 | 9.4 | N/S | N/S | N/S | 12 | 10 | 1151 | 162 | 3 | 0.2 | 14.44 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-04 | 2.71 | 7.5 | 8.6 | 14 | 6 | N/S | 10 | 9 | 1159 | 178 | 3 | 0.2 | 14.74 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-05 | 2.37 | 7.5 | 7.8 | 12 | 6 | <5 | 10 | 9 | 1101 | 134 | 3 | 0.2 | 17.34 | 2.1 | 0.005 | 7 | 0.7 | 6200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-06 | 2.21 | 7.5 | 8 | 12 | 6 | N/S | 9 | 8 | 1099 | 160 | 3 | 0.2 | 19.06 | 2.4 | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.017 | 0.1 | <0.1 | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 86 | 36 | 362 | N/S | <2.5 | 8
2012-03-07 | 2.07 | 7.5 | 7.2 | 12 | 8 | N/S | 11 | 11 | 1083 | 192 | 4 | 0.4 | 19.41 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-08 | 2.4 | 7.4 | 8.7 | 15 | 9 | N/S | 16 | 14 | 1148 | 196 | 4 | 0.2 | 18.72 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-09 | 2.51 | 7.6 | 6.6 | N/S | N/S | N/S | 18 | 14 | 1186 | 250 | 3 | 0.1 | 18.24 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-10 | 2.29 | 7.5 | 7.9 | N/S | N/S | N/S | 18 | 15 | 1075 | 208 | 4 | 0.1 | 18.1 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-11 | 2.01 | 7.5 | 7.3 | 16 | 8 | N/S | 14 | 12 | 1073 | 192 | 4 | 0.3 | 18.6 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-12 | 2.44 | 7.5 | 7.4 | 12 | 5 | <5 | 11 | 9 | 1111 | 232 | 3 | 0.2 | 17 | 2.3 | 0.006 | 7 | 0.7 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-13 | 2.75 | 7.4 | 7.5 | 11 | 6 | N/S | 13 | 9 | 1167 | 222 | 4 | 0.2 | 16.96 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.022 | 0.2 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.007 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 97 | 38 | 399 | N/S | <2.5 | 7
2012-03-14 | 2.29 | 7.4 | 6.5 | 12 | 7 | N/S | 9 | 9 | 1206 | 216 | 4 | 0.2 | 17.03 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-15 | 2.17 | 7.4 | 7.2 | 9 | 6 | N/S | 9 | 7 | 1336 | 286 | 3 | 0.8 | 18.26 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-16 | 1.74 | 7.4 | 6.9 | N/S | N/S | N/S | 12 | 8 | 1314 | 248 | 4 | 0.3 | 18.07 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-17 | 2.16 | 7.6 | 6.7 | N/S | N/S | N/S | 12 | 10 | 1171 | 190 | 5 | 1 | 17.1 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-18 | 1.83 | 7.7 | 6.8 | 15 | 8 | N/S | 11 | 9 | 1130 | 188 | 5 | 0.8 | 16.99 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-19 | 1.91 | 7.4 | 6.2 | 15 | 9 | <5 | 14 | 9 | 1106 | 186 | 4 | 0.5 | 18.81 | 2.8 | <0.005 | 9 | 0.9 | 35000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-20 | 2.16 | 7.3 | 7.8 | 20 | 8 | N/S | 13 | 12 | 1182 | 244 | 4 | 0.7 | 17.82 | 2.7 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.016 | 0.1 | N/S | <0.02 | 0.06 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 36 | 369 | N/S | <2.5 | 8
2012-03-21 | 1.84 | 7.5 | 6.7 | 16 | 6 | N/S | 11 | 9 | 1281 | 404 | 4 | 0.3 | 19.32 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-22 | 1.84 | 7.6 | 7.2 | 14 | 8 | N/S | 9 | 7 | 1099 | 178 | 4 | 0.3 | 21.31 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-23 | 3.06 | 7.5 | 7.1 | N/S | N/S | N/S | 11 | 9 | 1020 | 200 | 4 | 0.1 | 16.82 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-24 | 2.98 | 7.5 | 7.7 | N/S | N/S | N/S | 8 | 8 | 1002 | 190 | 3 | 0.1 | 13.21 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-25 | 2.89 | 7.5 | 7.6 | 10 | 5 | N/S | 14 | 11 | 1122 | 212 | 4 | 0.2 | 15.4 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-26 | 2.57 | 7.5 | 7.5 | 9 | 4 | <5 | 6 | 4 | 1045 | 158 | 3 | 0.2 | 16.86 | 2 | 0.005 | 6 | 0.7 | 110000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-27 | 2.1 | 7.6 | 8.7 | 9 | 5 | N/S | 9 | 8 | 1213 | 190 | 3 | 0.3 | 17.38 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | 0.002 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 93 | 37 | 385 | N/S | <5.0 | 6
2012-03-28 | 1.93 | 7.5 | 7.4 | 8 | 4 | N/S | 6 | 4 | 1197 | 172 | 3 | 0.5 | 18.76 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-29 | 1.95 | 7.5 | 6.5 | 8 | 3 | N/S | 6 | 5 | 1260 | 190 | 3 | 0.4 | 19.4 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-30 | 1.86 | 7.6 | 7.6 | N/S | N/S | N/S | 8 | 4 | 1310 | 254 | 3 | 0.2 | 20.17 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-03-31 | 1.9 | 7.5 | 7.6 | N/S | N/S | N/S | 7 | 4 | 1322 | 254 | 3 | 0.2 | 19.58 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-01 | 2.19 | 7.5 | 7.9 | 8 | 3 | N/S | 7 | 4 | 1272 | 246 | 3 | 0.2 | 19.18 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-02 | 2.42 | 7.6 | 6.3 | 8 | 4 | <5 | 7 | 5 | 1261 | 228 | 3 | 0.3 | 18.61 | 2.2 | <0.005 | <5 | 0.8 | 54000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-03 | 1.86 | 7.4 | 8.1 | 7 | 3 | N/S | 3 | 2 | 1302 | 218 | 3 | 0.5 | 19.61 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.032 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.023 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 102 | 40 | 419 | N/S | <5.0 | 5
2012-04-04 | 1.75 | 7.5 | 7.5 | 5 | <2 | N/S | 3 | 0 | 1256 | 152 | 3 | 0.3 | 19.66 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-05 | 1.85 | 7.6 | 6.2 | 9 | 3 | N/S | 6 | 4 | 1143 | 140 | 3 | 0.3 | 22.7 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-06 | 1.77 | 7.4 | 7.5 | N/S | N/S | N/S | 4 | 4 | 1054 | 154 | 3 | 0.8 | 20.79 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-07 | 1.91 | 7.5 | 7.7 | N/S | N/S | N/S | 4 | 2 | 1033 | 162 | 2 | 0.2 | 21.27 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-08 | 1.86 | 7.5 | 8 | 7 | 3 | N/S | 5 | 3 | 1000 | 142 | 3 | 0.3 | 22.19 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-09 | 1.6 | 7.5 | 7.6 | 8 | 4 | <5 | 4 | 4 | 1038 | 134 | 3 | 0.4 | 24.88 | 3.4 | <0.005 | 5 | 1 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-10 | 1.78 | 7.5 | 8.4 | 5 | 3 | N/S | 4 | 3 | 1158 | 206 | 2 | 0.3 | 23.74 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.007 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 91 | 36 | 375 | N/S | <2.5 | 6
2012-04-11 | 1.93 | 7.4 | 8.6 | 6 | 3 | N/S | 6 | 4 | 1278 | 210 | 2 | 0.2 | 23.59 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-12 | 1.72 | 7.4 | 8 | 5 | 4 | N/S | 4 | 4 | 1340 | 248 | 3 | 0.2 | 23.61 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-13 | 1.71 | 7.4 | 8.2 | N/S | N/S | N/S | 5 | 5 | 1360 | 240 | 3 | 0.3 | 24.98 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-14 | 1.84 | 7.4 | 7.6 | N/S | N/S | N/S | 5 | 5 | 1310 | 218 | 3 | 0.3 | 25.55 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-15 | 2.59 | 7.4 | 7.2 | 7 | 3 | N/S | 6 | 4 | 1130 | 180 | 3 | 0.2 | 20.77 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-16 | 3.17 | 7.3 | 7.1 | 8 | 2 | <5 | 4 | 3 | 1003 | 156 | 2 | 0.5 | 15.34 | 1.8 | 0.006 | <5 | 0.6 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-17 | 2.42 | 7.4 | 7.4 | 7 | 4 | N/S | 7 | 6 | 1127 | 202 | 2 | 0.2 | 17.97 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.023 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 81 | 32 | 336 | N/S | 2.8 | 6
2012-04-18 | 1.96 | 7.7 | 9.2 | 9 | 4 | N/S | 6 | 4 | 1148 | 128 | 4 | 0.3 | 21.77 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-19 | 1.9 | 7.4 | 7.1 | 9 | 5 | N/S | 8 | 6 | 1193 | 162 | 3 | 0.4 | 23.29 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-20 | 1.88 | 7.7 | 6.3 | N/S | N/S | N/S | 8 | 6 | 1226 | 196 | 4 | 0.3 | 23.62 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-21 | 1.93 | 7.4 | 7.6 | N/S | N/S | N/S | 9 | 7 | 1239 | 198 | 4 | 0.3 | 24.5 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-22 | 1.91 | 7.4 | 7.1 | 8 | 5 | N/S | 10 | 6 | 1203 | 184 | 4 | 0.4 | 22.68 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-23 | 1.77 | 7.5 | 6.8 | 10 | 5 | <5 | 7 | 7 | 1325 | 210 | 4 | 0.4 | 22.18 | 3.1 | 0.005 | 5 | 1 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-24 | 1.75 | 7.5 | 6.9 | 11 | 5 | N/S | 10 | 10 | 1326 | 256 | 4 | 0.4 | 23.73 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.016 | 0.1 | N/S | <0.02 | 0.019 | <0.2 | <0.005 | 0.029 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 92 | 34 | 369 | N/S | <2.5 | 7
2012-04-25 | 1.74 | 7.4 | 6.5 | 12 | 6 | N/S | 8 | 7 | 1257 | 144 | 3 | 0.5 | 23.48 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-26 | 1.74 | 7.5 | 7.8 | 12 | 6 | N/S | 10 | 8 | 1178 | 178 | 3 | 0.6 | 23.88 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-27 | 1.66 | 7.5 | 8.1 | N/S | N/S | N/S | 8 | 8 | 1250 | 220 | 4 | 0.4 | 24.23 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-28 | 2 | 7.5 | 8.2 | N/S | N/S | N/S | 8 | 6 | 1107 | 174 | 3 | 0.6 | 22.74 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-29 | 1.94 | 7.5 | 7 | 14 | T/X | N/S | 8 | 6 | 1196 | 226 | 4 | 0.8 | 19.17 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-04-30 | 2.26 | 7.4 | 7 | 11 | T/X | <5 | 6 | 4 | 1251 | 312 | 3 | 0.5 | 19.1 | 2.8 | <0.005 | <5 | 0.8 | 65000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-01 | 2.62 | 7.5 | 7 | 7 | 3 | N/S | 8 | 8 | 1162 | 284 | 3 | 0.7 | 18.06 | 2.4 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.008 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.028 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 78 | 31 | 322 | N/S | 2.6 | 6
2012-05-02 | 2.84 | 7.4 | 8 | 10 | 5 | N/S | 10 | 9 | 1122 | 288 | 3 | 0.3 | 17.54 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-03 | 2.58 | 7.6 | 6.6 | 8 | 5 | N/S | 8 | 5 | 1192 | 260 | 2 | 0.7 | 19.33 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-04 | 3.86 | 7.4 | 6.2 | N/S | N/S | N/S | 10 | 8 | 876 | 224 | 3 | 0.2 | 13.39 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-05 | 4.1 | 7.4 | 7.7 | N/S | N/S | N/S | 16 | 13 | 822 | 176 | 3 | 0.2 | 11.41 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-06 | 3.06 | 7.4 | 7.3 | 9 | 5 | N/S | 8 | 6 | 898 | 176 | 2 | 0.3 | 14.57 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-07 | 4.1 | 7.4 | 7.5 | 8 | 3 | <5 | 9 | 9 | 764 | 138 | 2 | 0.2 | 11.86 | 1.6 | <0.005 | <5 | 0.5 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-08 | 4.15 | 7.4 | 7.4 | 7 | 4 | N/S | 8 | 6 | 740 | 108 | 1 | 0.2 | 9.69 | 1.3 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | 0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | <0.001 | <0.2 | <0.005 | 0.018 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 71 | 30 | 300 | N/S | 8.1 | 6
2012-05-09 | 4.15 | 7.5 | 6.3 | 8 | 5 | N/S | 10 | 6 | 802 | 138 | 2 | 0.2 | 12.69 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-10 | 3.25 | 7.5 | 6.4 | 6 | 3 | N/S | 5 | 4 | 904 | 138 | 1 | 0.2 | 14.57 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-11 | 2.89 | 7.4 | 9 | N/S | N/S | N/S | 10 | 8 | 1058 | 232 | 2 | 0.2 | 17.24 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-12 | 2.61 | 7.4 | 7.2 | N/S | N/S | N/S | 6 | 4 | 1043 | 224 | 2 | 0.2 | 17.83 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-13 | 2.11 | 7.5 | 8.5 | 6 | 4 | N/S | 3 | 2 | 1156 | 302 | 2 | 0.3 | 19.37 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-14 | 2.32 | 7.5 | 6.3 | 5 | <2 | <5 | 6 | 4 | 1105 | 154 | 2 | 0.3 | 20.73 | 2.9 | <0.005 | <5 | 0.8 | 47000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-15 | 2.33 | 7.4 | 6 | 5 | 2 | N/S | 4 | 3 | 1083 | 180 | 2 | 0.2 | 20.08 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.028 | <0.001 | <0.005 | <0.005 | <0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.031 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 88 | 35 | 363 | N/S | <2.5 | 6
2012-05-16 | 1.9 | 7.5 | 8.6 | 6 | 3 | N/S | 4 | 3 | 1120 | 138 | 2 | 0.5 | 21.29 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-17 | 2.08 | 7.6 | 7.2 | 5 | 3 | N/S | 5 | 3 | 1227 | 248 | 2 | 0.3 | 22.9 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-18 | 2.03 | 7.7 | 7.1 | N/S | N/S | N/S | 4 | 4 | 1077 | 168 | 2 | 0.3 | 21.34 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-19 | 2.1 | 7.6 | 7.5 | N/S | N/S | N/S | 6 | 4 | 1103 | 190 | 2 | 0.3 | 20.63 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-20 | 2.09 | 7.6 | 7 | 4 | <2 | N/S | 5 | 5 | 1137 | 180 | 2 | 0.3 | 19.3 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-21 | 2.38 | 7.6 | 7.3 | 5 | 2 | <5 | 3 | 3 | 1111 | 174 | 2 | 0.3 | 18.8 | 2.8 | <0.005 | <5 | 0.9 | 51000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-22 | 2.04 | 7.6 | 6.9 | 5 | 3 | N/S | 6 | 5 | 1144 | 196 | 2 | 0.3 | 19.61 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.018 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 90 | 34 | 363 | N/S | <2.5 | 6
2012-05-23 | 1.96 | 7.5 | 6.9 | 5 | 3 | N/S | 8 | 4 | 1263 | 98 | 2 | 0.3 | 21.32 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-24 | 1.96 | 7.7 | 5.7 | 5 | 3 | N/S | 6 | 5 | 1178 | 156 | 2 | 0.3 | 22.27 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-25 | 1.94 | 7.5 | 6.3 | N/S | N/S | N/S | <4 | 4 | 1487 | 324 | 3 | 0.3 | 22.48 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-26 | 1.92 | 7.5 | 7.2 | N/S | N/S | N/S | 3 | 3 | 1552 | 348 | 2 | 0.3 | 22.2 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-27 | 1.82 | 7.5 | 6.6 | 5 | 3 | N/S | 7 | 6 | 1554 | 364 | 2 | 0.3 | 22.63 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-28 | 1.92 | 7.6 | 6.6 | 6 | 2 | <5 | 4 | 4 | 1623 | 386 | 3 | 0.5 | 22.13 | 3.7 | 0.005 | <5 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-29 | 1.89 | 7.5 | 6.2 | 6 | 2 | N/S | 6 | <4 | 1617 | 250 | 2 | 0.4 | 21.39 | 3.4 | N/S | N/S | N/S | 3500 | <0.05 | 0.042 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | 0.019 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 122 | 44 | 488 | N/S | <2.5 | 6
2012-05-30 | 1.79 | 7.5 | 6.6 | 6 | 2 | N/S | 4 | 4 | 1624 | 354 | 3 | 0.4 | 22.83 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-05-31 | 2.07 | 7.5 | 6.4 | 6 | 3 | N/S | 7 | 4 | 1518 | 302 | 3 | 0.3 | 22.19 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-01 | 2.91 | 7.5 | 6.5 | N/S | N/S | N/S | 9 | 7 | 1182 | 270 | 3 | 0.2 | 15.8 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-02 | 2.62 | 7.4 | 7.2 | N/S | N/S | N/S | 6 | 6 | 1179 | 250 | 2 | 0.2 | 16.85 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-03 | 2.56 | 7.4 | 7.4 | 6 | 4 | N/S | 5 | 3 | 1401 | 330 | 2 | 0.3 | 19.64 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-04 | 1.94 | 7.4 | 6.4 | 4 | 3 | <5 | 15 | 10 | 1497 | 334 | 3 | 0.3 | 21.13 | 3 | <0.005 | 8 | 0.9 | 5200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-05 | 1.88 | 7.4 | 6.4 | 5 | <2 | N/S | 4 | 4 | 1494 | 318 | 2 | 0.3 | 23.15 | 3.5 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.011 | 0.1 | <0.1 | <0.02 | 0.011 | <0.2 | <0.005 | 0.033 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 105 | 37 | 414 | N/S | 3 | 5
2012-06-06 | 1.79 | 7.4 | 7.2 | 5 | <2 | N/S | 5 | 2 | 1524 | 312 | 2 | 0.7 | 24.84 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-07 | 1.82 | 7.4 | 6.6 | 5 | <2 | N/S | 4 | 3 | 1614 | 416 | 3 | 0.3 | 23.75 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-08 | 1.79 | 7.4 | 6.3 | N/S | N/S | N/S | 4 | 2 | 1537 | 318 | 3 | 0.3 | 25.04 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-09 | 1.87 | 7.4 | 7.6 | N/S | N/S | N/S | <4 | <4 | 1524 | 300 | 3 | 0.5 | 22.64 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-10 | 1.82 | 7.3 | 6.4 | 7 | 4 | N/S | 4 | <4 | 1617 | 350 | 3 | 0.7 | 22.37 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-11 | 1.75 | 7.4 | 5.8 | 5 | 3 | <5 | 6 | 4 | 1671 | 394 | 3 | 0.4 | 23.3 | 3.5 | <0.005 | 6 | 1 | 95000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-12 | 1.75 | 7.5 | 5.8 | 6 | 4 | N/S | 10 | 8 | 1590 | 336 | 2 | 0.3 | 23.17 | 3.5 | N/S | N/S | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | 0.031 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 115 | 40 | 454 | N/S | <2.5 | 6
2012-06-13 | 1.76 | 7.5 | 6.2 | 5 | 2 | N/S | 4 | 4 | 1650 | 392 | 2 | 0.3 | 25.04 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-14 | 1.78 | 7.7 | 6.5 | 5 | 2 | N/S | <4 | <4 | 1751 | 466 | 2 | 0.3 | 25.25 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-15 | 1.75 | 7.5 | 6.2 | N/S | N/S | N/S | <4 | <4 | 1761 | 478 | 3 | 0.3 | 23.1 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-16 | 1.91 | 7.5 | 6.5 | N/S | N/S | N/S | 4 | 4 | 1828 | 508 | 2 | 0.3 | 23.11 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-17 | 2.4 | 7.5 | 6.4 | 5 | 3 | N/S | 4 | 4 | 1371 | 342 | 2 | 0.2 | 18.87 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-18 | 2.4 | 7.4 | 6.3 | 5 | T/X | <5 | <4 | <4 | 1437 | 366 | 2 | 0.3 | 20.11 | 3 | <0.005 | <5 | 0.8 | 5800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-19 | 1.79 | 7.5 | 6.2 | 3 | 2 | N/S | 4 | 4 | 1525 | 364 | 2 | 0.4 | 22.07 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.005 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.024 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 109 | 38 | 432 | N/S | <2.5 | 6
2012-06-20 | 1.81 | 7.4 | 5.8 | 3 | <2 | N/S | <4 | <4 | 1544 | 410 | 2 | 0.4 | 23.36 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-21 | 1.71 | 7.5 | 6.1 | 5 | 3 | N/S | 6 | 6 | 1689 | 422 | 2 | 0.3 | 24.09 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-22 | 1.76 | 7.5 | 6.8 | N/S | N/S | N/S | 5 | 4 | 1584 | 426 | 2 | 0.3 | 24.08 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-23 | 1.9 | 7.5 | 6 | N/S | N/S | N/S | 4 | 4 | 1838 | 498 | 2 | 0.3 | 23.52 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-24 | 1.76 | 7.4 | 6 | 2 | 2 | N/S | <4 | <4 | 1970 | 512 | 1 | 0.3 | 23.64 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-25 | 1.93 | 7.5 | 5.8 | 3 | <2 | <5 | 4 | <4 | 1902 | 472 | 2 | 0.3 | 24.7 | 3.6 | <0.005 | <5 | 1 | 7600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-26 | 1.73 | 7.5 | 6.8 | 5 | 2 | N/S | 4 | 4 | 2062 | 498 | 2 | 0.3 | 25.8 | 3.8 | N/S | N/S | N/S | N/S | <0.05 | 0.05 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.019 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 137 | 44 | 524 | N/S | 5.7 | 6
2012-06-27 | 1.79 | 7.5 | 7.1 | 4 | 3 | N/S | 6 | 5 | 2041 | 562 | 2 | 0.3 | 26.55 | 4.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-28 | 1.81 | 7.5 | 7.1 | 3 | 3 | N/S | 6 | 4 | 2075 | 494 | 2 | 0.4 | 25.58 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-29 | 1.86 | 7.5 | 6.5 | N/S | N/S | N/S | 6 | <4 | 2012 | 588 | 2 | 0.3 | 23.51 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-06-30 | 2.06 | 7.4 | 6.2 | N/S | N/S | N/S | 5 | 5 | 1501 | 390 | 2 | 0.2 | 19.84 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-01 | 1.73 | 7.4 | 6.2 | 8 | 4 | N/S | 7 | <4 | 1351 | 318 | 3 | 0.9 | 21.22 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-02 | 1.69 | 7.4 | 6 | 6 | 3 | <5 | 6 | 4 | 1310 | 264 | 2 | 0.8 | 21.61 | 3.2 | <0.005 | 6 | 0.9 | 5200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-03 | 1.7 | 7.5 | 5.8 | 6 | 4 | N/S | 7 | <4 | 1352 | 300 | 2 | 0.6 | 19.58 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.007 | 0.1 | <0.1 | <0.02 | 0.072 | <0.2 | <0.005 | 0.026 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 94 | 33 | 370 | N/S | <2.5 | 7
2012-07-04 | 1.68 | 7.4 | 4.5 | 6 | 5 | N/S | 5 | 4 | 1543 | 370 | 3 | 0.6 | 22.73 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-05 | 1.62 | 7.5 | 4.9 | 5 | 4 | N/S | 5 | 4 | 1651 | 430 | 2 | 0.7 | 24.97 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-06 | 1.7 | 7.4 | 5 | N/S | N/S | N/S | 6 | 5 | 1531 | 378 | 3 | 0.4 | 25.66 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-07 | 1.71 | 7.4 | 5 | N/S | N/S | N/S | 8 | 6 | 1591 | 442 | 2 | 0.4 | 24.85 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-08 | 1.74 | 7.4 | 6 | 9 | 5 | N/S | 15 | 14 | 1588 | 446 | 3 | 0.2 | 25.44 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-09 | 1.59 | 7.4 | 6.7 | 15 | 7 | <5 | 20 | 16 | 1724 | 498 | 5 | 1.6 | 27.19 | 4.2 | <0.005 | 16 | 1.1 | 7300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-10 | 1.48 | 7.5 | 5.5 | 8 | 6 | N/S | 13 | 10 | 1606 | 446 | 3 | 0.2 | 28.07 | 4 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.016 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.033 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 117 | 40 | 460 | N/S | 3 | 7
2012-07-11 | 1.42 | 7.4 | 6.5 | 9 | 5 | N/S | 13 | 10 | 1765 | 554 | 3 | 0.1 | 28.38 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-12 | 1.41 | 7.5 | 6.6 | 6 | 3 | N/S | 10 | 10 | 1646 | 488 | 2 | 0.1 | 24.1 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-13 | 1.42 | 7.5 | 6.2 | N/S | N/S | N/S | 15 | 12 | 1991 | 652 | 3 | 0.2 | 27.36 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-14 | 1.58 | 7.4 | 6.4 | N/S | N/S | N/S | 12 | 11 | 1855 | 602 | 3 | 0.5 | 24.86 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-15 | 1.48 | 7.5 | 6.1 | 9 | 5 | N/S | 11 | 10 | 1937 | 630 | 3 | 0.4 | 25.11 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-16 | 1.47 | 7.4 | 6.4 | 9 | 6 | <5 | 18 | 12 | 1839 | 560 | 3 | 0.3 | 25.38 | 3.4 | <0.005 | 5 | 1.1 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-17 | 1.51 | 7.5 | 5.9 | 11 | 7 | N/S | 13 | 10 | 1873 | 544 | 2 | 0.2 | 26.86 | 3.7 | N/S | N/S | N/S | N/S | <0.05 | 0.044 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.035 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 121 | 40 | 466 | N/S | 4.2 | 7
2012-07-18 | 1.66 | 7.5 | 5.4 | 10 | 6 | N/S | 11 | 9 | 2012 | 536 | 2 | 0.2 | 24.24 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-19 | 2.38 | 7.2 | 5.5 | 6 | 3 | N/S | 5 | 4 | 1144 | 272 | 2 | 0.1 | 16.87 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-20 | 2.27 | 7.3 | 6 | N/S | N/S | N/S | 6 | 6 | 1036 | 202 | 2 | 0.1 | 16.19 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-21 | 1.67 | 7.4 | 6.2 | N/S | N/S | N/S | 7 | 6 | 1296 | 306 | 2 | 0.1 | 19.79 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-22 | 1.57 | 7.5 | 5.8 | 9 | 5 | N/S | 11 | 10 | 1495 | 368 | 3 | 0.2 | 21.27 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-23 | 1.51 | 7.4 | 4.2 | 12 | 6 | <5 | 26 | 21 | 1560 | 424 | 3 | 0.1 | 24.56 | 3 | <0.005 | <5 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-24 | 1.99 | 7.5 | 5.9 | <2 | <2 | N/S | 9 | 9 | 1114 | 134 | 2 | <0.1 | 20.94 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.03 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 31 | 350 | N/S | 2.7 | 6
2012-07-25 | 1.87 | 7.5 | 6.4 | 8 | 4 | N/S | 9 | 9 | 1140 | 232 | 2 | <0.1 | 19.86 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-26 | 2.31 | 7.4 | 7.4 | 6 | 2 | N/S | 8 | 7 | 944 | 152 | 2 | 0.1 | 18.08 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-27 | 1.75 | 7.4 | 7.7 | N/S | N/S | N/S | 10 | 8 | 1029 | 222 | 2 | 0.1 | 18.29 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-28 | 1.73 | 7.5 | 6.8 | N/S | N/S | N/S | 6 | 6 | 1082 | 240 | 1 | 0.1 | 22.02 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-29 | 1.67 | 7.6 | 6.1 | 3 | <2 | N/S | 6 | 6 | 1111 | 224 | 1 | 0.1 | 23.05 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-30 | 1.66 | 7.6 | 5.8 | 6 | 3 | <5 | 4 | 4 | 1156 | 204 | 1 | 0.1 | 24.68 | 2.7 | <0.005 | <5 | 0.9 | 4600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-07-31 | 1.73 | 7.6 | 5.8 | 7 | <2 | N/S | 6 | 5 | 1145 | 226 | 1 | 0.2 | 25.57 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 81 | 29 | 320 | N/S | <2.5 | 6
2012-08-01 | 1.61 | 7.6 | 5.7 | 7 | 3 | N/S | 4 | <4 | 1237 | 272 | 2 | 0.1 | 25.76 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-02 | 1.56 | 7.5 | 5.9 | 5 | <2 | N/S | <4 | <4 | 1311 | 280 | 1 | 0.1 | 26.28 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-03 | 1.58 | 7.4 | 5.3 | N/S | N/S | N/S | 4 | <4 | 1351 | 336 | 1 | 0.1 | 25.62 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-04 | 1.85 | 7.4 | 7.6 | N/S | N/S | N/S | 6 | 6 | 1348 | 350 | 2 | <0.1 | 23.35 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-05 | 2.85 | 7.5 | 7.2 | 4 | <2 | N/S | 7 | 4 | 1102 | 242 | 2 | 0.1 | 16.19 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-06 | 2.09 | 7.6 | 5.2 | 6 | 2 | <5 | 4 | <4 | 1294 | 290 | 2 | 0.1 | 18.8 | 2.3 | <0.005 | <5 | 0.8 | 21000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-07 | 1.93 | 7.4 | 6.7 | 4 | <2 | N/S | <4 | <4 | 1487 | 350 | 1 | 0.1 | 22.33 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.011 | 0.1 | 0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.03 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 101 | 35 | 397 | N/S | <5 | 5
2012-08-08 | 1.61 | 7.5 | 5.8 | 5 | 3 | N/S | 4 | <4 | 1507 | 328 | 2 | 0.4 | 22.93 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-09 | 1.6 | 7.4 | 5.9 | 5 | <2 | N/S | 4 | <4 | 1380 | 228 | 1 | 0.1 | 24.98 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-10 | 1.57 | 7.4 | 5.7 | N/S | N/S | N/S | 4 | <4 | 1321 | 164 | 2 | 0.1 | 25.13 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-11 | 1.65 | 7.6 | 6.3 | N/S | N/S | N/S | 4 | <4 | 478 | 68 | 2 | 0.1 | 26.01 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-12 | 1.55 | 7.6 | 6.7 | 6 | T/X | N/S | 4 | 4 | 1289 | 188 | 1 | 0.1 | 26.37 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-13 | 1.81 | 7.6 | 5.4 | 4 | T/X | <5 | 4 | <4 | 1336 | 302 | 2 | 0.1 | 25.62 | 3.3 | <0.005 | <5 | 1 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-14 | 2.14 | 7.5 | 6.1 | 4 | 2 | N/S | 4 | <4 | 1192 | 222 | 1 | 0.2 | 22.53 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.005 | <0.2 | <0.005 | 0.018 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 28 | 315 | N/S | T/X | 6
2012-08-15 | 1.81 | 7.5 | 6.1 | 4 | <2 | N/S | <4 | <4 | 1177 | 188 | 2 | 0.1 | 22.95 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-16 | 2 | 7.4 | 6 | 4 | 3 | N/S | 6 | <4 | 1542 | 376 | 2 | 0.1 | 23.19 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-17 | 2.07 | 7.6 | 5.5 | N/S | N/S | N/S | <4 | <4 | 1311 | 282 | 2 | 0.1 | 22.03 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-18 | 1.69 | 7.5 | 6.5 | N/S | N/S | N/S | 4 | 4 | 1311 | 280 | 2 | 0.1 | 23.99 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-19 | 1.66 | 7.4 | 7 | 6 | 2 | N/S | 5 | 4 | 1322 | 264 | 2 | 0.1 | 25.47 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-20 | 1.75 | 7.6 | 5.8 | 4 | <2 | <5 | 6 | 4 | 1343 | 224 | 2 | 0.1 | 26.42 | 3.5 | 0.005 | <5 | 1.1 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-21 | 1.65 | 7.5 | 7.3 | 6 | 3 | N/S | 6 | 5 | 1439 | 292 | 2 | 0.2 | 26.93 | 3.7 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.03 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 94 | 32 | 366 | N/S | 6.3 | 7
2012-08-22 | 1.63 | 7.6 | 7.5 | 6 | 3 | N/S | 6 | <4 | 1406 | 260 | 2 | 0.3 | 27.93 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-23 | 1.62 | 7.6 | 5.4 | 5 | <2 | N/S | 9 | 5 | 1425 | 252 | 2 | 0.2 | 28.12 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-24 | 1.59 | 7.2 | 7 | N/S | N/S | N/S | 6 | 4 | 1437 | 296 | 2 | 0.2 | 28.12 | 4.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-25 | 1.67 | 7.6 | 6.5 | N/S | N/S | N/S | 6 | 5 | 1441 | 282 | 3 | 0.6 | 27.68 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-26 | 2.21 | 7.5 | 5.2 | 8 | 5 | N/S | 9 | 7 | 1723 | 422 | 2 | 0.4 | 22.29 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-27 | 4.06 | 7.5 | 5.1 | 6 | 4 | <5 | 10 | 7 | 842 | 190 | 3 | 0.1 | 11.78 | 1.4 | <0.005 | <5 | 0.5 | 25000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-28 | 3.53 | 7.4 | 5.3 | 7 | 3 | N/S | 8 | 7 | 890 | 194 | 2 | 0.3 | 11.23 | 1.3 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.013 | 0.2 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.032 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 74 | 26 | 293 | N/S | <8.0 | 7
2012-08-29 | 2.54 | 7.4 | 5.3 | 8 | 5 | N/S | 8 | 8 | 1161 | 218 | 4 | 1.3 | 14.84 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-30 | 1.91 | 7.5 | 6.1 | 7 | 2 | N/S | 6 | 5 | 1273 | 264 | 3 | 0.7 | 19.44 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-08-31 | 1.81 | 7.5 | 5.6 | N/S | N/S | N/S | 7 | 4 | 1331 | 292 | 3 | 0.4 | 22.66 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-01 | 2 | 7.6 | 6.7 | N/S | N/S | N/S | 7 | <4 | 1223 | 276 | 3 | 0.2 | 21.52 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-02 | 2.13 | 7.5 | 7.7 | 5 | 3 | N/S | 6 | 4 | 1115 | 238 | 2 | 0.2 | 17.84 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-03 | 1.89 | 7.5 | 6.4 | 5 | <2 | <5 | 4 | 4 | 1113 | 220 | 2 | 0.3 | 19.38 | 2.6 | <0.005 | 8 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-04 | 1.75 | 7.5 | 6.8 | 5 | <2 | N/S | 5 | 4 | 1209 | 246 | 2 | 0.1 | 20.47 | 2.7 | N/S | N/S | N/S | 2100 | <0.05 | 0.033 | <0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 31 | 346 | N/S | <4.0 | 7
2012-09-05 | 2.11 | 7.5 | 6.9 | 4 | <2 | N/S | 4 | <4 | 1111 | 212 | 2 | 0.1 | 21.77 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-06 | 1.82 | 7.5 | 6.3 | 4 | <2 | N/S | 4 | 4 | 1127 | 182 | 2 | 0.2 | 20.55 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-07 | 2 | 7.7 | 6.4 | N/S | N/S | N/S | <4 | <4 | 1055 | 198 | 3 | <0.1 | 20.83 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-08 | 1.99 | 7.5 | 5.5 | N/S | N/S | N/S | <4 | <4 | 982 | 186 | 2 | 0.1 | 20.35 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-09 | 2.11 | 7.5 | 6.1 | 3 | <2 | N/S | 6 | 4 | 922 | 172 | 2 | 0.1 | 20.89 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-10 | 1.72 | 7.6 | 6.1 | 8 | 3 | <5 | 6 | 6 | 958 | 144 | 2 | 0.1 | 22.84 | 3 | <0.005 | <5 | 1 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-11 | 1.66 | 7.5 | 6.3 | 3 | <2 | N/S | 6 | 6 | 1007 | 188 | 2 | 0.1 | 24.24 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.021 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 67 | 25 | 268 | N/S | <4.0 | 6
2012-09-12 | 1.61 | 7.5 | 5.8 | 4 | 3 | N/S | 9 | 6 | 916 | 82 | 2 | 0.1 | 25.89 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-13 | 1.63 | 7.5 | 6.2 | 4 | <2 | N/S | <4 | <4 | 962 | 162 | 2 | 0.1 | 25.64 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-14 | 1.93 | 7.5 | 5.5 | N/S | N/S | N/S | 4 | 4 | 996 | 180 | 2 | 0.1 | 24.95 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-15 | 1.75 | 7.5 | 5.6 | N/S | N/S | N/S | <4 | <4 | 1080 | 192 | 2 | 0.1 | 23.81 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-16 | 1.73 | 7.5 | 7.8 | 3 | 3 | N/S | 4 | <4 | 1127 | 178 | 2 | 0.1 | 21.6 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-17 | 1.76 | 7.5 | 7.3 | 3 | <2 | <5 | <4 | <4 | 1136 | 138 | 2 | 0.1 | 22.75 | 2.9 | <0.005 | 5 | 1.1 | 970 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-18 | 1.93 | 7.5 | 7.2 | 4 | <2 | N/S | 5 | 4 | 1101 | 220 | 2 | 0.1 | 22.14 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.005 | <0.2 | <0.005 | 0.023 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 30 | 343 | N/S | <4.0 | 6
2012-09-19 | 1.67 | 7.5 | 6.7 | 4 | <2 | N/S | 5 | 5 | 1124 | 168 | 3 | 0.1 | 23.79 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-20 | 1.66 | 7.5 | 6 | 4 | 2 | N/S | 5 | <4 | 1123 | 218 | 2 | 0.1 | 25.43 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-21 | 1.58 | 7.5 | 6.2 | N/S | N/S | N/S | 6 | 6 | 1148 | 204 | 2 | 0.1 | 25.57 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-22 | 1.68 | 7.6 | 6.6 | N/S | N/S | N/S | 5 | 5 | 1114 | 200 | 2 | 0.1 | 27.33 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-23 | 1.67 | 7.6 | 6.1 | 7 | 3 | N/S | 6 | 6 | 1062 | 180 | 2 | 0.1 | 26.7 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-24 | 1.56 | 7.6 | 5.6 | 6 | <2 | <5 | 8 | 6 | 1071 | 146 | 2 | 0.2 | 27.41 | 3.4 | <0.005 | 5 | 1.2 | 1100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-25 | 1.55 | 7.6 | 6 | 5 | 3 | N/S | 6 | 5 | 1059 | 138 | 2 | 0.2 | 27.57 | 3.4 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.016 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.022 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 79 | 28 | 313 | N/S | <4.0 | 7
2012-09-26 | 1.52 | 7.6 | 5.9 | 5 | 3 | N/S | 9 | 7 | 1088 | 118 | 3 | 0.2 | 28.67 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-27 | 1.56 | 7.5 | 5.1 | 7 | 3 | N/S | 8 | 7 | 1228 | 180 | 3 | 0.2 | 29.19 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-28 | 1.51 | 7.4 | 4.7 | N/S | N/S | N/S | 8 | 8 | 1354 | 252 | 3 | 0.2 | 29 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-29 | 1.61 | 7.5 | 4.8 | N/S | N/S | N/S | 10 | 9 | 1404 | 290 | 3 | 0.2 | 29.23 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-09-30 | 1.62 | 7.6 | 5 | 8 | 3 | N/S | 9 | 9 | 1465 | 302 | 3 | 0.2 | 28.21 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-01 | 1.53 | 7.3 | 4.8 | 9 | 5 | <5 | 7 | 6 | 1434 | 292 | 3 | 0.1 | 27.71 | 3.5 | <0.005 | <5 | 1.2 | 2900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-02 | 1.49 | 7.5 | 5.9 | 7 | 4 | N/S | 6 | 5 | 1419 | 248 | 3 | 0.2 | 28.72 | 3.6 | N/S | N/S | N/S | N/S | <0.05 | 0.013 | <0.001 | <0.005 | 0.014 | 0.1 | 0.1 | <0.02 | 0.012 | <0.2 | <0.005 | 0.021 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 58 | 20 | 229 | N/S | <4.0 | 7
2012-10-03 | 1.43 | 7.5 | 6.5 | 6 | 3 | N/S | 7 | 6 | 1348 | 156 | 3 | 0.5 | 26.84 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-04 | 1.59 | 7.4 | 5.9 | 4 | 3 | N/S | 5 | 4 | 1311 | 164 | 2 | 0.2 | 28.29 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-05 | 1.45 | 7.6 | 5.7 | N/S | N/S | N/S | 4 | 4 | 1265 | 164 | 2 | 0.1 | 27.01 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-06 | 1.53 | 7.6 | 6.3 | N/S | N/S | N/S | 4 | 4 | 1246 | 168 | 2 | 0.1 | 27.66 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-07 | 1.55 | 7.5 | 6.1 | 3 | 3 | N/S | 4 | 4 | 1289 | 180 | 2 | 0.2 | 27.1 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-08 | 1.51 | 7.5 | 8.8 | 4 | <2 | <5 | 5 | 4 | 1320 | 166 | 2 | 0.1 | 27.87 | 3.2 | <0.005 | <5 | 1.2 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-09 | 1.52 | 7.4 | 5.4 | 5 | 2 | N/S | 5 | <4 | 1265 | 164 | 2 | 0.2 | 27.37 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.015 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.039 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 90 | 30 | 348 | N/S | 10.6 | 5
2012-10-10 | 1.65 | 7.4 | 6.5 | 4 | 2 | N/S | 6 | 5 | 1205 | 158 | 3 | 0.2 | 26.29 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-11 | 1.53 | 7.4 | 6.3 | 7 | 4 | N/S | 5 | <4 | 1167 | 134 | 2 | 0.2 | 27.06 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-12 | 1.45 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | 4 | 1161 | 142 | 3 | 0.2 | 28.23 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-13 | 1.96 | 7.4 | 8.2 | N/S | N/S | N/S | 8 | 6 | 1056 | 134 | 3 | 0.4 | 26.52 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-14 | 2.5 | 7.3 | 6.2 | 5 | 2 | N/S | 6 | 4 | 850 | 124 | 3 | 0.1 | 18.46 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-15 | 2.45 | 7.3 | 7 | 4 | 3 | <5 | 6 | <4 | 826 | 112 | 2 | 0.2 | 17 | 2.1 | 0.008 | <5 | 0.8 | 1600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-16 | 1.67 | 7.4 | 6.6 | 4 | 3 | N/S | 5 | <4 | 940 | 148 | 2 | 0.1 | 21.91 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.031 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 69 | 25 | 274 | N/S | <4.0 | 7
2012-10-17 | 1.61 | 7.3 | 7.9 | 7 | 3 | N/S | 10 | 6 | 950 | 128 | 3 | 0.2 | 24.18 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-18 | 2.7 | 7.4 | 7.2 | 8 | 4 | N/S | 10 | 8 | 794 | 118 | 2 | 0.1 | 19.14 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-19 | 2.39 | 7.3 | 6.5 | N/S | N/S | N/S | 6 | 4 | 896 | 152 | 2 | 0.1 | 17.25 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-20 | 1.9 | 7.5 | 6.3 | N/S | N/S | N/S | 6 | 4 | 966 | 178 | 2 | 0.2 | 18.61 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-21 | 1.81 | 7.5 | 6.1 | 5 | 3 | N/S | 5 | 4 | 1065 | 172 | 2 | 0.2 | 21.16 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-22 | 2.05 | 7.5 | 5.5 | 6 | 3 | <5 | 7 | 5 | 942 | 128 | 2 | 0.4 | 22.85 | 2.8 | 0.006 | <5 | 1 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-23 | 1.98 | 7.4 | 6.3 | 6 | 4 | N/S | 5 | 5 | 852 | 92 | 2 | 0.2 | 22.84 | 3 | N/S | N/S | N/S | N/S | <0.05 | 0.027 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.017 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 67 | 24 | 265 | N/S | <4.0 | 7
2012-10-24 | 2.03 | 7.4 | 6.1 | 3 | <2 | N/S | 6 | <4 | 822 | 114 | 2 | 0.3 | 21.46 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-25 | 1.76 | 7.4 | 7 | 3 | 2 | N/S | 6 | <4 | 842 | 118 | 2 | 0.2 | 23.35 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-26 | 2.71 | 7.4 | 5.2 | N/S | N/S | N/S | 9 | 7 | 750 | 114 | 2 | 0.1 | 16.7 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-27 | 2.74 | 7.3 | 6 | N/S | N/S | N/S | 12 | 8 | 884 | 122 | 2 | 0.1 | 16.85 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-28 | 1.93 | 7.3 | 6 | 9 | 5 | N/S | 15 | 12 | 926 | 154 | 3 | 0.1 | 20.37 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-29 | 1.66 | 7.5 | 7 | 10 | 3 | <5 | 14 | 10 | 944 | 162 | 3 | 0.1 | 23.67 | 3.1 | <0.005 | <5 | T/X | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-10-30 | 1.67 | 7.5 | 6.8 | 10 | 5 | N/S | 18 | 13 | 1051 | 154 | 3 | 0.1 | 24.32 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.015 | 0.2 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.036 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 28 | 314 | N/S | 7.2 | 7
2012-10-31 | 1.53 | 7.3 | 9 | 11 | 4 | N/S | 19 | 16 | 1011 | 144 | 3 | 0.1 | 27.02 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-01 | 1.58 | 7.5 | 7.4 | 8 | 5 | N/S | 12 | 10 | 936 | 178 | 3 | 0.2 | 27.54 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-02 | 1.58 | 7.5 | 7.3 | N/S | N/S | N/S | 13 | 9 | 1029 | 142 | 3 | 0.2 | 25.54 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-03 | 1.67 | 7.4 | 6.7 | N/S | N/S | N/S | 13 | 10 | 1059 | 146 | 3 | 0.8 | 25.71 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-04 | 1.7 | 7.3 | 6.5 | 13 | 6 | N/S | 14 | 10 | 1025 | 144 | 4 | 1.7 | 24.97 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-05 | 1.58 | 7.5 | 6.2 | 9 | 5 | <5 | 11 | 9 | 1063 | 146 | 4 | 1.1 | 23.69 | 3.6 | 0.006 | 5 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-06 | 1.6 | 7.4 | 6.4 | 10 | 4 | N/S | 10 | 8 | 1041 | 154 | 3 | 0.6 | 27.1 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.016 | 0.1 | <0.1 | <0.02 | 0.011 | <0.2 | <0.005 | 0.014 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 79 | 27 | 308 | N/S | 5.2 | 8
2012-11-07 | 1.67 | 7.2 | 7 | 9 | 6 | N/S | 12 | 9 | 1012 | 136 | 3 | 0.6 | 26.31 | 3.2 | N/S | N/S | N/S | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-08 | 1.57 | 7.2 | 7.3 | 9 | 4 | N/S | 11 | 8 | 976 | 118 | 3 | 0.3 | 25.63 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-09 | 1.54 | 7.2 | 8.7 | N/S | N/S | N/S | 9 | 8 | 1018 | 148 | 3 | 0.3 | 25.95 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-10 | 2 | 7.5 | 7.7 | N/S | N/S | N/S | 12 | 11 | 988 | 146 | 5 | 2 | 23.84 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-11 | 2.04 | 7.3 | 7.3 | 12 | 5 | N/S | 12 | 10 | 858 | 138 | 4 | 1.8 | 19.01 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-12 | 2.49 | 7.4 | 4.5 | 9 | T/X | <5 | 14 | 11 | 778 | 100 | 3 | 0.3 | 15.95 | 2.1 | 0.006 | 18 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-13 | 2.24 | 7.2 | 6.8 | 9 | 6 | N/S | 12 | 9 | 848 | 100 | 2 | 0.2 | 18.08 | 1.9 | N/S | N/S | N/S | 13000 | <0.05 | 0.027 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.019 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 69 | 25 | 275 | N/S | 4.7 | 6
2012-11-14 | 1.62 | 7.3 | 8.7 | 9 | 5 | N/S | 11 | 8 | 970 | 148 | 3 | 0.1 | 20.81 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-15 | 1.65 | 7.5 | 7.4 | 9 | 6 | N/S | 13 | 10 | 1051 | 142 | 4 | 0.2 | 23.01 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-16 | 1.62 | 7.5 | 7.1 | N/S | N/S | N/S | 8 | 8 | 1043 | 138 | 7 | 0.3 | 22.71 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-17 | 1.71 | 7.4 | 7.3 | N/S | N/S | N/S | 7 | 6 | 1079 | 120 | 6 | 0.8 | 22.73 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-18 | 1.68 | 7.4 | 6.9 | 11 | 5 | N/S | 7 | 7 | 1100 | 122 | 4 | 1.1 | 23.67 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-19 | 1.56 | 7.4 | 6.2 | 8 | 4 | <5 | 6 | 4 | 1075 | 152 | 3 | 0.5 | 24 | 2.9 | <0.005 | 5 | 1.2 | 9500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-20 | 1.52 | 7.4 | 6.8 | 7 | 4 | N/S | 6 | 5 | 1054 | 154 | 2 | 0.2 | 25.27 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 79 | 27 | 307 | N/S | <4.0 | 7
2012-11-21 | 1.59 | 7.4 | 6.8 | 8 | 4 | N/S | <4 | <4 | 1098 | 142 | 3 | 0.5 | 26.46 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-22 | 1.7 | 7.5 | 6.6 | 8 | 5 | N/S | 9 | 6 | 1147 | 144 | 4 | 1.9 | 23.74 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-23 | 1.58 | 7.4 | 6.3 | N/S | N/S | N/S | 10 | 7 | 1197 | 168 | 4 | 1.1 | 23.78 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-24 | 1.68 | 7.3 | 7.6 | N/S | N/S | N/S | 6 | 5 | 1161 | 160 | 3 | 0.7 | 27.12 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-25 | 1.66 | 7.5 | 8.2 | 11 | 7 | N/S | 10 | 7 | 1117 | 138 | 3 | 0.5 | 25.03 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-26 | 1.59 | 7.4 | 7.9 | 10 | 5 | <5 | 8 | 6 | 1059 | 108 | 3 | 0.3 | 26.32 | 3.4 | <0.005 | <5 | 1.2 | 31000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-27 | 1.56 | 7.4 | 8.4 | 9 | T/X | N/S | 10 | 9 | 1102 | 138 | 3 | 0.2 | 27.6 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.023 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 26 | 308 | N/S | <4.0 | 7
2012-11-28 | 1.58 | 7.4 | 9.8 | 9 | 4 | N/S | 10 | 7 | 1088 | 150 | 3 | 0.2 | 28.5 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-29 | 1.52 | 7.3 | 9.4 | 11 | 5 | N/S | 10 | 8 | 1218 | 244 | 3 | 0.3 | 28.56 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-11-30 | 1.48 | 7.3 | 7.3 | N/S | N/S | N/S | 14 | 12 | 1141 | 186 | 4 | 0.3 | 29.45 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-01 | 1.6 | 7.4 | 7.2 | N/S | N/S | N/S | 19 | 16 | 1163 | 204 | 6 | 1.3 | 28.62 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-02 | 1.58 | 7.3 | 5.2 | 15 | 11 | N/S | 18 | 14 | 1112 | 202 | 7 | 2 | 26.75 | 4.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-03 | 1.45 | 7.4 | 5.8 | 10 | 7 | <5 | 9 | 8 | 1063 | 134 | 4 | 1.1 | 26.54 | 3.3 | 0.006 | <5 | 1.2 | 140000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-04 | 1.5 | 7.4 | 6.1 | 9 | 6 | N/S | 10 | 10 | 1002 | 124 | 3 | 0.3 | 25.1 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.005 | 0.016 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.034 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 68 | 24 | 270 | N/S | <4.0 | 8
2012-12-05 | 1.49 | 7.3 | 6.3 | 11 | 7 | N/S | 15 | 12 | 960 | 134 | 4 | 0.2 | 27.16 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-06 | 1.49 | 7.4 | 6.8 | 12 | 7 | N/S | 13 | 10 | 952 | 146 | 3 | 0.3 | 27.67 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-07 | 1.47 | 7.4 | 7 | N/S | N/S | N/S | 9 | 7 | 1003 | 190 | 3 | 0.3 | 27.3 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-08 | 1.75 | 7.3 | 6.5 | N/S | N/S | N/S | 10 | 9 | 1036 | 178 | 3 | 0.4 | 26.37 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-09 | 1.76 | 7.4 | 8 | 13 | 6 | N/S | 11 | 8 | 1057 | 182 | 4 | 1 | 25.37 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-10 | 1.71 | 7.3 | 7.5 | 12 | 5 | <5 | 13 | 9 | 1106 | 192 | 3 | 0.4 | 25.08 | 3.1 | 0.006 | <5 | 1.1 | 5400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-11 | 1.52 | 7.4 | 7 | 14 | 5 | N/S | 12 | 8 | 1096 | 152 | 3 | 0.3 | 25.84 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.049 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 94 | 31 | 361 | N/S | <4.0 | 8
2012-12-12 | 1.49 | 7.3 | 8.8 | 16 | 7 | N/S | 16 | 15 | 1269 | 194 | 4 | 0.4 | 27.56 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-13 | 1.52 | 7.3 | 7.7 | 16 | 7 | N/S | 17 | 13 | 1313 | 198 | 3 | 0.7 | 25.63 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-14 | 1.52 | 7.4 | 6.4 | N/S | N/S | N/S | 13 | 8 | 1302 | 172 | 3 | 0.2 | 23.52 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-15 | 1.75 | 7.4 | 7.1 | N/S | N/S | N/S | 13 | 10 | 1197 | 158 | 3 | 0.3 | 23.1 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-16 | 2.08 | 7.3 | 6.1 | 22 | 6 | N/S | 12 | 10 | 984 | 116 | 4 | 1.9 | 19.08 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-17 | 1.62 | 7.4 | 5.9 | 14 | 5 | <5 | 8 | 6 | 1103 | 140 | 3 | 1.1 | 20.81 | 2.7 | 0.005 | <5 | 1 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-18 | 1.57 | 7.4 | 6.1 | 10 | 5 | N/S | 6 | 5 | 1354 | 202 | 3 | 0.3 | 24.18 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | 0.054 | 0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 91 | 31 | 354 | N/S | <8.0 | 6
2012-12-19 | 1.53 | 7.4 | 6.4 | 10 | 4 | N/S | 10 | 8 | 1308 | 184 | 3 | 0.2 | 29.08 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-20 | 3.81 | 7.3 | 6.4 | 11 | 6 | N/S | 15 | 12 | 752 | 112 | 2 | 0.1 | 16.27 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-21 | 4.32 | 7.5 | 7.3 | N/S | N/S | N/S | 12 | 10 | 626 | 114 | 2 | <0.1 | 10.85 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-22 | 2.72 | 7.3 | 9.7 | N/S | N/S | N/S | 6 | 4 | 726 | 110 | 1 | 0.1 | 12.24 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-23 | 2.44 | 7.5 | 8.6 | 9 | 4 | N/S | 7 | 7 | 818 | 142 | 2 | 0.1 | 16.55 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-24 | 2.39 | 7.5 | 7.8 | 7 | 4 | <5 | 8 | 6 | 830 | 122 | 2 | <0.1 | 17.67 | 2.2 | <0.005 | 7 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-25 | 2.11 | 7.5 | 7.5 | 11 | 5 | N/S | 6 | 5 | 838 | 138 | 2 | 0.6 | 19.61 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.012 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 68 | 26 | 278 | N/S | <8.0 | 7
2012-12-26 | 1.73 | 7.5 | 7.6 | 9 | 5 | N/S | 5 | 4 | 836 | 114 | 2 | 0.4 | 22.02 | 2.8 | N/S | N/S | N/S | 200000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-27 | 1.78 | 7.4 | 7.7 | 7 | 5 | N/S | 8 | 5 | 842 | 114 | 2 | 0.1 | 22.02 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-28 | 1.77 | 7.5 | 7.2 | N/S | N/S | N/S | 6 | 5 | 836 | 122 | 2 | <0.1 | 21.75 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-29 | 1.74 | 7.5 | 7.1 | N/S | N/S | N/S | 6 | 6 | 848 | 144 | 2 | 0.1 | 21.54 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-30 | 1.99 | 7.5 | 7.5 | 8 | 6 | N/S | 7 | 7 | 838 | 124 | 4 | 1.4 | 21.69 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2012-12-31 | 1.78 | 7.4 | 6 | 12 | 6 | <5 | 5 | <4 | 880 | 134 | 3 | 1.1 | 20.91 | 2.9 | <0.005 | <5 | 1.2 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
Reporting Limit (RL) |  |  |  | 2 | 2 | 5 | 4 | 4 | 100 |  | 1 | 0.1 | 0.15 | 0.1 | 0.005 | 5 | 0.1 | 10 | 0.05 | 0.004 | 0.001 | 0.005 | 0.005 | 0.1 | 0.1 | 0.02 | 0.001 | 0.2 | 0.005 | 0.005 | 0.001 | 0.01 | 0.05 | 0.001 | 0.1 | 6 | 1 | 1 |  |  | 0.5* | 1
Observations | 366 | 366 | 366 | 262 | 255 | 53 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 53 | 53 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 51 | 52
Minimum | 1.41 | 7.2 | 4.2 | <2 | <2 | <5 | <4 | <4 | 478 | 68 | 1 | <0.1 | 9.08 | 0.8 | <0.005 | <5 | 0.4 | 970 | <0.05 | 0.013 | <0.001 | <0.005 | <0.005 | <0.1 | <0.1 | <0.02 | <0.001 | <0.2 | <0.005 | 0.012 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 58 | 20 | 229 |  | <2.5 | 4
Mean | 2.03 | 7.5 | 7 | <8 | <4 | <5 | <8 | <6 | 1229 | 225 | 3 | <0.3 | 21.62 | 2.8 | <0.005 | <6 | 0.9 | 30624 | <0.05 | 0.034 | <0.001 | <0.005 | <0.011 | <0.1 | <0.1 | <0.02 | <0.012 | <0.2 | <0.005 | 0.022 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 89 | 33 | 358 |  | <3.9 | 6
Maximum | 4.32 | 7.7 | 10 | 22 | 11 | <5 | 26 | 21 | 2075 | 652 | 7 | 2 | 29.45 | 4.2 | 0.008 | 18 | 1.2 | 350000 | <0.05 | 0.05 | 0.001 | <0.005 | 0.032 | 0.2 | 0.1 | <0.02 | 0.072 | <0.2 | <0.005 | 0.054 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 137 | 44 | 524 |  | 10.6 | 8
Std Dev | 0.54 | 0.1 | 1.1 | 3 | 2 | 0 | 4 | 3 | 261 | 104 | 1 | 0.3 | 4.16 | 0.7 | 0.001 | 3 | 0.2 | 59844 | 0 | 0.006 | 0 | 0 | 0.005 | 0 | 0.1 | 0 | 0.012 | 0 | 0 | 0.012 | 0 | 0.01 | 0 | 0 | 0 | 0 | 16 | 6 | 61 |  | 2 | 1
.
* LL Hg: Based on the sample matrix some samples need to be diluted x2, x5 and x10. The reporting limit
of 0.5 ng/L for LL Hg will then change by the same factor resulting in reporting limits of 1.0, 2.5, and 5.0 ng/L respectively.
January 8, 2012 BOD5, CBOD5: Batch failed QA standard; analysis exempt from rerun.
April 3 and 10, 2012 As, Ba, Cd, Cr, Cu, Fe, Pb, Mn, Ni, Se, Ag, Zn, Sb, Be, Tl, Ca and Mg: LOQ standard expired.
April 17, 2012 As, Ba, Cd, Cr, Cu, Fe, Pb, Mn, Ni, Se, Ag, Zn, Sb, Be and Tl: LOQ standard expired.
April 23, 2012 Phenol: Sample/aliquot not chemically preserved.
April 29-30, 2012 BOD5: Batch failed QA standard; analysis exempt from rerun. Result not used for DMR reporting.
April 29-30, 2012 CBOD5, T/X: Batch failed QA standard.
June 18, 2012 BOD5: Batch failed QA standard; analysis exempt from rerun. Result not used for DMR reporting.
August 12-13, 2012 CBOD5, T/X: Batch failed QA standard.
August 14, 2012 LL Hg, T/X: QA failure.
October 2, 2012 Hg: Aliquot not preserved; added prior to analysis.
October 29, 2012 F, T/X: Aliquot never arrived at laboratory.
November 5, 2012 F, T/X: Aliquot never arrived at laboratory.
November 12 and 27, 2012 BOD5: Batch failed QA standard; analysis exempt from rerun.
November 12 and 27, 2012 CBOD5, T/X: Batch failed QA standard.
December 24, 2012 F, T/X: Aliquot never arrived at laboratory.
December 31, 2012 FEC COL, T/X: Sample not analyzed due to holiday.

## Lemont Outfall 2013
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg Sol | *Low Level Hg | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | ng/L | mg/L
2013-01-01 | 1.69 | 7.5 | 6.9 | 13 | 6 | N/S | 7 | 6 | 862 | 122 | 3 | 0.7 | 21.5 | 3.4 | N/S | N/S | N/S | N/S | <0.05 | 0.028 | <0.001 | <0.005 | 0.01 | 0.1 | 0.1 | <0.02 | 0.014 | <0.2 | <0.005 | 0.035 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 78 | 28 | 311 | N/S | N/S | 7
2013-01-02 | 1.62 | 7.5 | 7.2 | 11 | T/X | N/S | 8 | 8 | 822 | 122 | 2 | 0.3 | 23.08 | 3.2 | N/S | N/S | N/S | 8100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | <5.0 | N/S
2013-01-03 | 1.72 | 7.3 | 7 | 11 | 5 | N/S | 6 | 5 | 868 | 152 | 3 | 0.2 | 22.8 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-04 | 1.66 | 7.3 | 7.7 | N/S | N/S | N/S | 8 | 7 | 816 | 132 | 3 | <0.1 | 21.99 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-05 | 1.78 | 7.5 | 8.4 | N/S | N/S | N/S | 9 | 8 | 880 | 146 | 4 | 1.6 | 21.41 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-06 | 1.79 | 7.4 | 9 | 17 | 7 | N/S | 9 | 8 | 912 | 126 | 4 | 1.6 | 20.5 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-07 | 1.66 | 7.5 | 8 | 13 | 6 | <5 | 8 | 7 | 938 | 152 | 3 | 0.3 | 21.94 | T/X | <0.005 | 14 | 1.2 | 36000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-08 | 1.63 | 7.6 | 7.3 | 12 | 6 | N/S | 6 | 6 | 978 | 160 | 3 | <0.1 | 22.66 | T/X | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | 0.013 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 90 | 31 | 352 | N/S | <8.0 | 7
2013-01-09 | 1.64 | 7.3 | 9.3 | 14 | 6 | N/S | 10 | 10 | 1064 | 204 | 3 | 0.2 | 23 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-10 | 1.71 | 7.7 | 7.8 | 17 | 6 | N/S | 14 | 11 | 982 | 156 | 4 | 0.2 | 27.38 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-11 | 3.47 | 7.5 | 8.7 | N/S | N/S | N/S | 14 | 12 | 848 | 164 | 3 | <0.1 | 16.84 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-12 | 2.53 | 7.5 | 7.5 | N/S | N/S | N/S | 9 | 9 | 836 | 140 | 2 | <0.1 | 13.32 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-13 | 3.03 | 7.4 | 8.2 | 14 | 7 | N/S | 15 | 12 | 902 | 126 | 3 | 0.2 | 14.52 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-14 | 2.53 | 7.4 | 6.7 | 10 | 5 | T/X | 11 | 8 | 946 | 146 | 3 | 0.1 | 16.71 | 1.8 | <0.005 | 5 | 0.8 | 240000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-15 | 2.3 | 7.4 | 7 | 15 | 7 | N/S | 17 | 14 | 930 | 146 | 3 | 0.4 | 18.32 | 2.3 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | 0.025 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 71 | 28 | 291 | N/S | <8.0 | 6
2013-01-16 | 1.85 | 7.4 | 7.6 | 14 | 6 | N/S | 12 | 10 | 950 | 136 | 4 | 0.3 | 18.93 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-17 | 1.8 | 7.4 | 6.6 | 11 | 6 | N/S | 14 | 11 | 952 | 178 | 3 | 0.2 | 19.93 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-18 | 1.72 | 7.3 | 9.2 | N/S | N/S | N/S | 13 | 9 | 912 | 180 | 4 | 0.1 | 20.86 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-19 | 1.83 | 7.4 | 7 | N/S | N/S | N/S | 15 | 10 | 940 | 178 | 4 | 1 | 18.28 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-20 | 1.82 | 7.4 | 7.3 | 15 | 9 | N/S | 13 | 11 | 944 | 138 | 4 | 0.7 | 19.6 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-21 | 1.8 | 7.4 | 7 | 14 | 7 | <5 | 15 | 12 | 962 | 154 | 4 | 0.3 | 21.43 | 2.9 | 0.006 | 6 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-22 | 1.76 | 7.4 | 8.2 | 15 | 7 | N/S | 16 | 15 | 948 | 124 | 3 | 0.2 | 20.76 | 2.5 | N/S | N/S | N/S | 5000 | <0.05 | 0.029 | <0.001 | <0.005 | 0.015 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.032 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 77 | 28 | 307 | N/S | <8.0 | 7
2013-01-23 | 1.72 | 7.4 | 7.3 | 12 | 6 | N/S | 14 | 12 | 972 | 150 | 3 | 0.1 | 21.23 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-24 | 1.61 | 7.4 | 8.7 | 17 | 7 | N/S | 21 | 15 | 946 | 150 | 4 | 0.1 | 21 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-25 | 1.56 | 7.6 | 7.2 | N/S | N/S | N/S | 26 | 22 | 1013 | 180 | 4 | 0.2 | 21.19 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-26 | 1.68 | 7.4 | 7.5 | N/S | N/S | N/S | 17 | 13 | 1023 | 180 | 4 | 0.8 | 20.18 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-27 | 1.83 | 7.4 | 6.9 | 21 | 7 | N/S | 21 | 18 | 1131 | 206 | 5 | 1.9 | 18.19 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-28 | 2.39 | 7.4 | 5.9 | 17 | 9 | <5 | 20 | 16 | 1824 | 186 | 4 | 0.8 | 16.02 | 2.3 | 0.008 | 9 | 0.9 | 40000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-29 | 2.99 | 7.4 | 7.1 | 14 | 7 | N/S | 17 | 13 | 1426 | 174 | 3 | 0.4 | 19.24 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.017 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | 0.033 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 78 | 29 | 315 | N/S | <8.0 | 6
2013-01-30 | 4.18 | 7.3 | 7.6 | 15 | 8 | N/S | 23 | 18 | 798 | 100 | 3 | 0.1 | 8.82 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-01-31 | 4.06 | 7.4 | 9.2 | 22 | T/X | N/S | 21 | 15 | 874 | 120 | 1 | 0.3 | 11.13 | 0.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-01 | 4.06 | 7.3 | 8.2 | N/S | N/S | N/S | 31 | 22 | 970 | 172 | 2 | 0.2 | 12.7 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-02 | 3.07 | 7.2 | 7.2 | N/S | N/S | N/S | 31 | 22 | 1063 | 150 | 3 | 2.2 | 14.06 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-03 | 2.2 | 7.3 | 7.5 | N/A | 15 | N/S | 27 | 21 | 1148 | 158 | 6 | 2.7 | 16.76 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-04 | 1.98 | 7.5 | 7.2 | 24 | 14 | 6 | 23 | 20 | 1186 | 144 | 5 | 1.8 | 18.7 | 2.6 | 0.007 | <5 | 0.9 | 50000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-05 | 1.87 | 7.5 | 7.7 | 21 | 11 | N/S | 20 | 16 | 1273 | 170 | 4 | 0.4 | 19.96 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.029 | 0.1 | 0.1 | <0.02 | 0.011 | <0.2 | <0.005 | 0.025 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 87 | 33 | 352 | N/S | <8.0 | 7
2013-02-06 | 1.83 | 7.4 | 6.6 | 13 | 10 | N/S | 17 | 12 | 1238 | 166 | 3 | 0.3 | 20.8 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-07 | 2.7 | 7.4 | 7 | 15 | 9 | N/S | 16 | 13 | 1520 | 184 | 3 | 0.4 | 17.14 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-08 | 3.68 | 7.3 | 8.2 | N/S | N/S | N/S | 10 | 8 | 1664 | 206 | 2 | 0.2 | 10.46 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-09 | 3.51 | 7.3 | 7.5 | N/S | N/S | N/S | 9 | 6 | 1599 | 200 | 2 | 0.5 | 12.39 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-10 | 2.98 | 7.4 | 7.4 | 8 | 6 | N/S | 6 | 6 | 1453 | 182 | 2 | 0.3 | 12.7 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-11 | 4.21 | 7.3 | 7.5 | 8 | 6 | <5 | 9 | 7 | 1392 | 190 | 2 | 0.2 | 10.88 | 1 | 0.008 | <5 | 0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-12 | 3.66 | 7.3 | 8.1 | 10 | 7 | N/S | 10 | 9 | 1370 | 182 | 2 | 0.3 | 13.34 | 1.2 | N/S | N/S | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.022 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 87 | 34 | 358 | N/S | <8.0 | 5
2013-02-13 | 2.41 | 7.6 | 7.3 | 9 | 6 | N/S | 10 | 7 | 1281 | 158 | 2 | 0.3 | 15.73 | 1.8 | N/S | N/S | N/S | 8400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-14 | 2.24 | 7.4 | 8.3 | 9 | 6 | N/S | 11 | 8 | 1222 | 158 | 3 | 0.3 | 17.52 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-15 | 2.11 | 7.4 | 7.7 | N/S | N/S | N/S | 11 | 8 | 1205 | 166 | 3 | 0.4 | 19.25 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-16 | 2.16 | 7.5 | 8 | N/S | N/S | N/S | 16 | 12 | 1163 | 160 | 4 | 0.4 | 19.05 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-17 | 2.02 | 7.3 | 9 | 10 | 6 | N/S | 12 | 10 | 1103 | 146 | 3 | 0.6 | 19.62 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-18 | 2.17 | 7.5 | 7.8 | 15 | 6 | <5 | 18 | 16 | 1075 | 150 | 4 | 0.8 | 19.05 | 2.8 | 0.008 | <5 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-19 | 2.38 | 7.5 | 8.2 | 11 | 6 | N/S | 12 | 8 | 1142 | 138 | 3 | 0.3 | 17.43 | 2.2 | N/S | N/S | N/S | 8700 | <0.05 | 0.035 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.03 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 31 | 326 | N/S | <8.0 | 6
2013-02-20 | 2.01 | 7.4 | 10.5 | 9 | 6 | N/S | 9 | 8 | 1217 | 178 | 3 | 0.2 | 17.61 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-21 | 1.88 | 7.3 | 9.4 | 10 | 6 | N/S | 11 | 9 | 1166 | 168 | 3 | 0.2 | 20.05 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-22 | 1.79 | 7.4 | 9.8 | N/S | N/S | N/S | 10 | 8 | 1175 | 166 | 3 | 0.4 | 20.44 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-23 | 1.91 | 7.5 | 7.7 | N/S | N/S | N/S | 11 | 9 | 1287 | 156 | 4 | 1.6 | 19.71 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-24 | 1.94 | 7.5 | 7.8 | 15 | 8 | N/S | 13 | 9 | 1281 | 144 | 5 | 2.5 | 18.35 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-25 | 1.94 | 7.5 | 7.2 | 13 | 6 | <5 | 8 | 6 | 1268 | 140 | 4 | 1 | 18.86 | 2.6 | 0.014 | 6 | 1.1 | 35000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-26 | 2.5 | 7.5 | 7.5 | 11 | 7 | N/S | 10 | 8 | 1651 | 164 | 3 | 0.7 | 16.89 | 2.4 | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.034 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 86 | 32 | 348 | N/S | <8.0 | 5
2013-02-27 | 2.72 | 7.3 | 9.5 | 7 | 6 | N/S | 10 | 8 | 2471 | 198 | 3 | 0.2 | 14.18 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-02-28 | 2.62 | 7.4 | 9 | 8 | 6 | N/S | 8 | 5 | 2353 | 228 | 2 | 0.3 | 13.91 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-01 | 2.33 | 7.5 | 8.2 | N/S | N/S | N/S | 8 | 6 | 2365 | 264 | 2 | 0.1 | 14.66 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-02 | 2.24 | 7.4 | 12.2 | N/S | N/S | N/S | 10 | 8 | 2036 | 228 | 2 | 0.4 | 14.56 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-03 | 2.18 | 7.5 | 9.2 | 9 | 5 | N/S | 7 | 5 | 1633 | 170 | 3 | 0.7 | 13.48 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-04 | 2.01 | 7.5 | 10.5 | 8 | 5 | <5 | 8 | 6 | 1452 | 158 | 3 | 0.3 | 15.79 | 2.2 | 0.012 | <5 | 1 | 2500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-05 | 2.09 | 7.3 | 10.5 | 8 | 4 | N/S | 8 | 8 | 1464 | 144 | 3 | 0.3 | 17.17 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.012 | 0.1 | 0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.03 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 84 | 33 | 345 | N/S | <8.0 | 5
2013-03-06 | 2.26 | 7.5 | 7.1 | 7 | 4 | N/S | 6 | <4 | 2273 | 228 | 2 | 0.3 | 16.84 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-07 | 2.36 | 7.5 | 8.6 | 8 | 4 | N/S | 9 | 7 | 2489 | 292 | 2 | 0.3 | 16.55 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-08 | 2.49 | 7.3 | 9 | N/S | N/S | N/S | 5 | 5 | 2120 | 238 | 1 | 0.3 | 15.4 | 0.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-09 | 2.92 | 7.3 | 7.7 | N/S | N/S | N/S | 6 | 6 | 1887 | 220 | 3 | 1.1 | 13.71 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-10 | 4.07 | 7.2 | 8.8 | 7 | 4 | N/S | 7 | 7 | 1197 | 166 | 2 | 0.1 | 7.58 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-11 | 4.27 | 7.2 | 10 | 7 | 5 | <5 | 7 | 5 | 822 | 130 | 2 | 0.1 | 5.92 | 0.6 | 0.008 | <5 | 0.3 | 8400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-12 | 4.09 | 7 | 10 | 6 | 4 | N/S | 4 | 4 | 1007 | 136 | 2 | 0.1 | 8.75 | 0.8 | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.005 | 0.1 | N/S | <0.02 | 0.005 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 72 | 29 | 298 | N/S | <8.0 | 5
2013-03-13 | 4.21 | 7.1 | 10 | 5 | 4 | N/S | 4 | <4 | 1161 | 160 | 2 | 0.1 | 10.77 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-14 | 3.72 | 7.1 | 10 | 7 | 3 | N/S | 4 | <4 | 1167 | 136 | 3 | 0.7 | 11.8 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-15 | 2.94 | 7.3 | 9 | N/S | N/S | N/S | 5 | 4 | 1231 | 152 | 2 | 0.8 | 12.98 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-16 | 2.26 | 7.4 | 9 | N/S | N/S | N/S | 5 | 4 | 1225 | 132 | 3 | 1 | 12.88 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-17 | 2.52 | 7.3 | 8.5 | 7 | 4 | N/S | 5 | <4 | 1223 | 130 | 3 | 1.3 | 13.61 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-18 | 2.48 | 7.2 | 9.4 | 7 | 3 | <5 | 4 | <4 | 1255 | 150 | 3 | 0.6 | 15.17 | 1.7 | 0.006 | 7 | 0.8 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-19 | 2.37 | 7.3 | 7.7 | 5 | 3 | N/S | <4 | <4 | 1295 | 146 | 3 | 0.3 | 15.24 | 1.6 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.035 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 93 | 36 | 381 | N/S | <8.0 | 6
2013-03-20 | 2.01 | 7.3 | 10 | 5 | 3 | N/S | 4 | <4 | 1274 | 136 | 2 | 0.3 | 16.75 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-21 | 2.09 | 7.2 | 8.2 | 6 | 3 | N/S | 6 | 4 | 1268 | 192 | 3 | 0.2 | 16.76 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-22 | 2.01 | 7.3 | 7.8 | N/S | N/S | N/S | 8 | 6 | 1231 | 158 | 3 | 0.2 | 17.9 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-23 | 2.02 | 7.4 | 8.4 | N/S | N/S | N/S | 7 | 6 | 1186 | 140 | 3 | 0.5 | 17.35 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-24 | 1.93 | 7.4 | 8.2 | 6 | 3 | N/S | <4 | <4 | 1192 | 150 | 3 | 0.7 | 17.79 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-25 | 1.9 | 7.3 | 6.6 | 8 | 5 | <5 | 6 | 4 | 1228 | 144 | 3 | 0.4 | 18.41 | 2.3 | 0.006 | 6 | 1 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-26 | 1.83 | 7.3 | 8.2 | 8 | 4 | N/S | 6 | <4 | 1277 | 148 | 2 | 0.2 | 19.54 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.034 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 89 | 34 | 365 | N/S | <8.0 | 6
2013-03-27 | 1.92 | 7.4 | 7.8 | 7 | 5 | N/S | 6 | 4 | 1281 | 176 | 2 | 0.2 | 19.29 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-28 | 1.96 | 7.3 | 7.7 | 4 | 3 | N/S | <4 | <4 | 1202 | 152 | 2 | 0.2 | 19.15 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-29 | 2 | 7.3 | 8.6 | N/S | N/S | N/S | 4 | <4 | 1169 | 136 | 3 | 0.5 | 19.55 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-30 | 2.16 | 7.3 | 8.7 | N/S | N/S | N/S | 4 | 4 | 1163 | 136 | 4 | 1.4 | 17.84 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-03-31 | 2.08 | 7.2 | 8 | 7 | 5 | N/S | 4 | <4 | 1139 | 144 | 4 | 1.4 | 17.36 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-01 | 1.99 | 7.3 | 8 | 6 | 3 | <5 | 4 | <4 | 1085 | 100 | 2 | 0.5 | 20.16 | 2.5 | <0.005 | 6 | 1.1 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-02 | 1.92 | 7.4 | 9.9 | 7 | 4 | N/S | 7 | 4 | 1083 | 118 | 3 | 0.3 | 19.52 | 2.7 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.011 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.038 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 85 | 33 | 347 | N/S | <8.0 | 4
2013-04-03 | 1.88 | 7.4 | 8.7 | 8 | 4 | N/S | 7 | 4 | 1024 | 138 | 3 | 0.2 | 21.97 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-04 | 1.87 | 7.3 | 8.8 | 8 | T/X | N/S | 5 | 5 | 1032 | 150 | 3 | 0.2 | 22.04 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-05 | 1.84 | 7.3 | 10 | N/S | N/S | N/S | 7 | 4 | 1036 | 204 | 4 | 0.2 | 22.84 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-06 | 1.97 | 7.4 | 9.6 | N/S | N/S | N/S | 5 | <4 | 1085 | 178 | 4 | 1.5 | 20.14 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-07 | 2.15 | 7.4 | 9.7 | 15 | 4 | N/S | 8 | 4 | 1161 | 186 | 4 | 1.9 | 19.22 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-08 | 3.05 | 7.4 | 7.7 | 10 | 4 | <5 | 8 | 5 | 1043 | 172 | 3 | 0.7 | 16.5 | 2.2 | <0.005 | 5 | 0.8 | 7500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-09 | 2.69 | 7.3 | 8.1 | 7 | 4 | N/S | 7 | 5 | 1187 | 192 | 3 | 0.2 | 15.49 | 1.9 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.017 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | 0.032 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 89 | 34 | 362 | N/S | <8.0 | 4
2013-04-10 | 3.04 | 7.5 | 8.1 | 7 | 4 | N/S | 6 | 4 | 1077 | 156 | 2 | 0.2 | 14.45 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-11 | 4.34 | 7.2 | 9.5 | 6 | 4 | N/S | 5 | 4 | 810 | 136 | 2 | <0.1 | 9.6 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-12 | 4.5 | 7.2 | 9.4 | N/S | N/S | N/S | 8 | 7 | 866 | 114 | 2 | <0.1 | 10.36 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-13 | 4.5 | 7.2 | 9 | N/S | N/S | N/S | 7 | 5 | 930 | 138 | 2 | 0.1 | 11.32 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-14 | 3.82 | 7.2 | 9.2 | 7 | 4 | N/S | 5 | 4 | 1039 | 160 | 2 | 0.3 | 12.32 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-15 | 3.37 | 7.3 | 7.6 | 6 | 3 | <5 | 4 | <4 | 1178 | 226 | 2 | 0.4 | 13.33 | 1.6 | 0.005 | 5 | 0.7 | 3300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-16 | 3.53 | 7.3 | 7.6 | 5 | 3 | N/S | <4 | <4 | 1103 | 226 | 2 | 0.1 | 12.35 | 1.4 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.012 | 0.2 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.028 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 79 | 32 | 332 | N/S | <8.0 | 5
2013-04-17 | 3.47 | 7.3 | 9.7 | 5 | 3 | N/S | 6 | <4 | 920 | 128 | 5 | 0.3 | 13.4 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-18 | 4.26 | 7.2 | 8.4 | 5 | 3 | N/S | 8 | 6 | 502 | 104 | 1 | 0.2 | 6.14 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-19 | 4.37 | 7.4 | 8.9 | N/S | N/S | N/S | 7 | 4 | 678 | 130 | 1 | <0.1 | 7.12 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-20 | 4.42 | 7.3 | 8.6 | N/S | N/S | N/S | 6 | 5 | 942 | 194 | 2 | 0.1 | 10 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-21 | 4.33 | 7.3 | 8.1 | 5 | 3 | N/S | 5 | 4 | 984 | 182 | 2 | 0.1 | 11.74 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-22 | 4.05 | 7.3 | 7.9 | 5 | 3 | <5 | <4 | <4 | 986 | 140 | 2 | 0.2 | 12.52 | 1 | <0.005 | <5 | 0.6 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-23 | 3.65 | 7.3 | 7.5 | 5 | 4 | N/S | 5 | <4 | 1036 | 162 | 2 | 0.2 | 14.11 | 1.3 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.021 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 86 | 35 | 357 | N/S | <8.0 | 6
2013-04-24 | 4.18 | 7.3 | 8.4 | 4 | 3 | N/S | 6 | 4 | 876 | 136 | 2 | 0.1 | 11.1 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-25 | 4.29 | 7.2 | 8.2 | 5 | 3 | N/S | 6 | 5 | 968 | 176 | 2 | 0.1 | 11.98 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-26 | 3.56 | 7.3 | 8.8 | N/S | N/S | N/S | 6 | 4 | 1096 | 220 | 2 | 0.1 | 14.2 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-27 | 3.14 | 7.2 | 8.8 | N/S | N/S | N/S | 6 | 4 | 1194 | 238 | 2 | 0.2 | 15.03 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-28 | 2.78 | 7.4 | 9.5 | 5 | 3 | N/S | 6 | 6 | 1186 | 218 | 2 | 0.2 | 15.94 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-29 | 2.53 | 7.4 | 7.5 | 4 | 3 | <5 | 4 | <4 | 1166 | 184 | 3 | 0.1 | 16.87 | 1.8 | 0.007 | 5 | 0.8 | 6800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-04-30 | 2.4 | 7.3 | 9.8 | 6 | 3 | N/S | 6 | 4 | 1175 | 180 | 3 | 0.1 | 17.42 | 1.9 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | 0.017 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 96 | 39 | 401 | N/S | <8.0 | 6
2013-05-01 | 2.22 | 7.4 | 7.4 | 5 | 3 | N/S | 6 | 6 | 1158 | 160 | 3 | 0.2 | 17.85 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-02 | 2.23 | 7.4 | 7.8 | 5 | 3 | N/S | 4 | <4 | 1190 | 174 | 3 | 0.1 | 18.62 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-03 | 2.18 | 7.4 | 7.8 | N/S | N/S | N/S | 4 | <4 | 1212 | 198 | 2 | 0.1 | 18.23 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-04 | 2.14 | 7.5 | 8.1 | N/S | N/S | N/S | 4 | 4 | 1234 | 206 | 2 | 0.1 | 18.91 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-05 | 2.27 | 7.5 | 8.1 | 7 | 4 | N/S | 8 | 6 | 1242 | 212 | 3 | 0.3 | 19.13 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-06 | 2.08 | 7.5 | 7.2 | 8 | 4 | <5 | 9 | 8 | 1326 | 210 | 3 | 0.2 | 20.26 | 2.9 | <0.005 | <5 | 1 | 5800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-07 | 2.04 | 7.5 | 7.8 | 8 | 3 | N/S | 8 | 8 | 1358 | 272 | 3 | 0.1 | 21.74 | 2.7 | N/S | N/S | N/S | N/S | 0.05 | 0.041 | <0.001 | <0.005 | 0.012 | 0.1 | <0.1 | <0.02 | 0.005 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 38 | 405 | N/S | <8.0 | 6
2013-05-08 | 2.02 | 7.3 | 7 | 9 | 4 | N/S | 11 | 9 | 1356 | 280 | 3 | 0.1 | 22.21 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-09 | 2.05 | 7.4 | 8.2 | 14 | 5 | N/S | 14 | 11 | 1311 | 196 | 3 | 0.1 | 22.12 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-10 | 2.52 | 7.2 | 6.5 | N/S | N/S | N/S | 13 | 12 | 1206 | 210 | 4 | 0.1 | 19.13 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-11 | 2.19 | 7.5 | 9.4 | N/S | N/S | N/S | 7 | 6 | 1225 | 190 | 3 | 0.1 | 19.39 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-12 | 2.16 | 7.5 | 7.3 | 19 | 7 | N/S | 14 | 14 | 1260 | 212 | 5 | 0.5 | 19.73 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-13 | 2.01 | 7.4 | 7.4 | 12 | 6 | <5 | 10 | 8 | 1325 | 246 | 3 | 0.2 | 21.53 | 2.8 | <0.005 | 5 | 1 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-14 | 1.95 | 7.5 | 8.2 | 12 | 7 | N/S | 12 | 11 | 1355 | 198 | 4 | 0.2 | 20.74 | 3 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | 0.027 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 97 | 36 | 392 | N/S | <8.0 | 6
2013-05-15 | 1.94 | 7.5 | 8.4 | 9 | 5 | N/S | 10 | 8 | 1385 | 266 | 3 | 0.2 | 20.61 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-16 | 1.91 | 7.3 | 7.9 | 8 | 4 | N/S | 7 | 6 | 1521 | 348 | 2 | 0.2 | 20.77 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-17 | 1.91 | 7.4 | 7.7 | N/S | N/S | N/S | 10 | 7 | 1542 | 342 | 2 | 0.1 | 20.94 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-18 | 2 | 7.4 | 6.3 | N/S | N/S | N/S | 12 | 10 | 1482 | 304 | 2 | 0.3 | 20.35 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-19 | 1.98 | 7.4 | 5.9 | 8 | 5 | N/S | 10 | 8 | 1440 | 264 | 3 | 0.3 | 19.95 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-20 | 1.92 | 7.5 | 6 | 11 | 6 | <5 | 11 | 10 | 1363 | 194 | 3 | 0.3 | 19.46 | 3.2 | <0.005 | 6 | 1 | 1800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-21 | 3.54 | 7.3 | 6.1 | 13 | 7 | N/S | 13 | 10 | 1007 | 170 | 5 | 0.1 | 14.25 | 2.3 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.015 | 0.2 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.041 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 81 | 30 | 326 | N/S | <8.0 | 6
2013-05-22 | 3.52 | 7.3 | 6.9 | 17 | 10 | N/S | 21 | 17 | 1011 | 166 | 4 | 0.1 | 13.64 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-23 | 3.3 | 7.3 | 7.3 | 14 | 9 | N/S | 13 | 9 | 1136 | 232 | 3 | 0.1 | 13.83 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-24 | 2.39 | 7.4 | 8.5 | N/S | N/S | N/S | 12 | 9 | 1166 | 216 | 3 | 0.2 | 15.31 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-25 | 2.18 | 7.4 | 8 | N/S | N/S | N/S | 10 | 8 | 1250 | 234 | 4 | 0.1 | 16.72 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-26 | 2.04 | 7.5 | 7.2 | 9 | 6 | N/S | 7 | 5 | 1268 | 220 | 3 | 0.3 | 18.1 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-27 | 2.2 | 7.5 | 7.5 | 9 | 5 | <5 | 7 | 6 | 1225 | 208 | 4 | 0.8 | 17.89 | 2.8 | 0.005 | 6 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-28 | 3.51 | 7.3 | 7.3 | 8 | 6 | N/S | 7 | 7 | 942 | 142 | 3 | 0.2 | 13.02 | 1.8 | N/S | N/S | N/S | 20000 | <0.05 | 0.031 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.026 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 72 | 28 | 295 | N/S | 11.2 | 7
2013-05-29 | 4.39 | 7.3 | 8.2 | 7 | 6 | N/S | 7 | 7 | 662 | 102 | 2 | 0.1 | 8.38 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-30 | 4.49 | 7.3 | 7.3 | 6 | 5 | N/S | 7 | 6 | 782 | 110 | 2 | 0.1 | 9.74 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-05-31 | 4.49 | 7.3 | 7.4 | N/S | N/S | N/S | 6 | 5 | 786 | 124 | 1 | 0.1 | 10.18 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-01 | 3.74 | 7.4 | 6.5 | N/S | N/S | N/S | 6 | 4 | 912 | 162 | 1 | 0.1 | 12.23 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-02 | 3.47 | 7.3 | 6.8 | 6 | 4 | N/S | 4 | 4 | 982 | 170 | 1 | 0.1 | 14.22 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-03 | 2.99 | 7.4 | 7.7 | 6 | 3 | <5 | 9 | 7 | 1102 | 180 | <1 | 0.2 | 15.52 | 1.8 | <0.005 | <5 | 0.7 | 5900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-04 | 2.27 | 7.5 | 6.9 | 5 | 3 | N/S | 6 | 5 | 1145 | 186 | <1 | 0.1 | 17.62 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.007 | 0.1 | <0.1 | <0.02 | 0.006 | <0.2 | <0.005 | 0.024 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 92 | 36 | 379 | N/S | <8.0 | 5
2013-06-05 | 2.1 | 7.3 | 7.9 | 4 | 3 | N/S | 6 | 4 | 1216 | 196 | 2 | 0.3 | 19.5 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-06 | 2.09 | 7.2 | 9 | 5 | 3 | N/S | 4 | <4 | 1233 | 204 | 2 | 0.2 | 20.32 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-07 | 2.03 | 7.3 | 7.5 | N/S | N/S | N/S | 6 | <4 | 1298 | 230 | 1 | 0.2 | 19.57 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-08 | 1.94 | 7.3 | 8 | N/S | N/S | N/S | 7 | 7 | 1304 | 214 | <1 | 0.2 | 19.41 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-09 | 1.91 | 7.2 | 8 | 6 | 3 | N/S | 8 | 6 | 1301 | 218 | <1 | 0.3 | 20.19 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-10 | 2.36 | 7.3 | 8.2 | 6 | 4 | <5 | 4 | <4 | 1225 | 194 | 3 | 0.2 | 19.33 | 2.5 | 0.005 | <5 | 0.9 | 5000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-11 | 2.01 | 7.3 | 7.2 | 5 | 4 | N/S | 6 | 5 | 1244 | 212 | 2 | 0.2 | 19.54 | 2.4 | N/S | N/S | N/S | N/S | 0.08 | 0.038 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.066 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 94 | 34 | 376 | N/S | <8.0 | 6
2013-06-12 | 2.31 | 7.4 | 6.8 | 7 | 4 | N/S | 6 | 6 | 1093 | 162 | 3 | 0.2 | 19.02 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-13 | 4.25 | 7.3 | 8.1 | 6 | 3 | N/S | 8 | 6 | 722 | 136 | 2 | 0.1 | 9.8 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-14 | 4.25 | 7.3 | 8.2 | N/S | N/S | N/S | 10 | 7 | 828 | 150 | 2 | <0.1 | 10.5 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-15 | 3.71 | 7.3 | 6.3 | N/S | N/S | N/S | 8 | 6 | 1006 | 186 | 3 | 0.1 | 12.76 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-16 | 2.51 | 7.4 | 6.2 | 6 | 4 | N/S | 4 | 4 | 1158 | 218 | 2 | 0.1 | 16.41 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-17 | 2.17 | 7.4 | 6.3 | 6 | 3 | <5 | 5 | 4 | 1178 | 196 | 3 | 0.2 | 19.33 | 2.4 | <0.005 | <5 | 0.8 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-18 | 2.01 | 7.4 | 6.5 | 7 | 4 | N/S | 6 | 6 | 1276 | 236 | 3 | 0.2 | 20.4 | 2.6 | N/S | N/S | N/S | N/S | 0.05 | 0.041 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.034 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 36 | 399 | N/S | <8.0 | 5
2013-06-19 | 1.9 | 7.4 | 7.8 | 9 | 6 | N/S | 12 | 8 | 1374 | 252 | 4 | 0.2 | 21.26 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-20 | 1.85 | 7.3 | 5.8 | 8 | 5 | N/S | 8 | 7 | 1416 | 262 | 3 | 0.2 | 21.48 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-21 | 2 | 7.4 | 6 | N/S | N/S | N/S | 9 | 7 | 1366 | 246 | 3 | 0.2 | 21.59 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-22 | 1.98 | 7.4 | 8 | N/S | N/S | N/S | 8 | 6 | 1244 | 230 | 4 | 0.2 | 21.08 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-23 | 1.94 | 7.3 | 7.5 | T/X | T/X | N/S | 12 | 9 | 1217 | 232 | 3 | 0.2 | 21.87 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-24 | 2.14 | 7.4 | 6.8 | 9 | 5 | <5 | 12 | 10 | 1194 | 214 | 3 | 0.2 | 20.33 | 3.2 | <0.005 | <5 | 0.9 | 6900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-25 | 2.14 | 7.4 | 7.6 | 7 | 4 | N/S | 10 | 7 | 1072 | 196 | 3 | 0.2 | 18.59 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.035 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 83 | 30 | 333 | N/S | <10.0 | 7
2013-06-26 | 2.62 | 7.4 | 7.4 | 7 | 5 | N/S | 10 | 8 | 1076 | 212 | 3 | 0.2 | 18.13 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-27 | 2.28 | 7.4 | 7 | 7 | 5 | N/S | 8 | 7 | 1033 | 194 | 3 | 0.2 | 16.7 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-28 | 2 | 7.3 | 7.5 | N/S | N/S | N/S | 12 | 9 | 1116 | 190 | 4 | 0.2 | 18.82 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-29 | 2.27 | 7.4 | 6.2 | N/S | N/S | N/S | 9 | 8 | 1154 | 210 | 2 | 0.2 | 19.4 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-06-30 | 1.97 | 7.5 | 5.9 | 6 | 4 | N/S | 6 | 4 | 1108 | 174 | 2 | 0.2 | 19.49 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-01 | 1.81 | 7.5 | 6.2 | 6 | 4 | <5 | 4 | 4 | 1167 | 202 | 2 | 0.3 | 20.64 | 2.6 | <0.005 | <5 | 0.9 | 24000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-02 | 1.76 | 7.5 | 6.1 | 4 | 4 | N/S | 6 | 5 | 1218 | 184 | 2 | 0.3 | 21.71 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | <0.005 | 0.1 | 0.1 | <0.02 | 0.006 | <0.2 | <0.005 | 0.041 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 96 | 34 | 382 | N/S | <8.0 | 5
2013-07-03 | 1.75 | 7.5 | 6.4 | 4 | 4 | N/S | 5 | <4 | 1242 | 216 | 2 | 0.4 | 22.84 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-04 | 1.72 | 7.5 | 6.3 | 5 | 4 | N/S | 5 | <4 | 1217 | 224 | 2 | 0.3 | 22.99 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-05 | 1.69 | 7.3 | 7.5 | N/S | N/S | N/S | 7 | 6 | 1216 | 212 | 2 | 0.4 | 24.4 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-06 | 1.69 | 7.5 | 7.2 | N/S | N/S | N/S | 7 | 7 | 1325 | 262 | 2 | 0.3 | 23.88 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-07 | 1.72 | 7.3 | 7.4 | 5 | 3 | N/S | 5 | 4 | 1332 | 274 | 2 | 0.3 | 23.76 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-08 | 2.1 | 7.5 | 7.2 | 5 | 4 | T/X | 4 | 4 | 1177 | 224 | 3 | 0.3 | 22.17 | 3 | <0.005 | <5 | 1 | 23000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-09 | 1.84 | 7.4 | 6 | 4 | 3 | N/S | 5 | <4 | 1148 | 208 | 2 | 0.2 | 18.83 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.018 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 93 | 33 | 368 | N/S | <8.0 | 5
2013-07-10 | 1.71 | 7.5 | 8.3 | 3 | 3 | N/S | <4 | <4 | 1137 | 206 | 2 | 0.3 | 23.27 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-11 | 1.71 | 7.5 | 7 | 4 | 4 | N/S | <4 | <4 | 1294 | 246 | 2 | 0.3 | 23.84 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-12 | 1.65 | 7.4 | 7.5 | N/S | N/S | N/S | 5 | <4 | 1404 | 296 | 3 | 0.3 | 24.7 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-13 | 1.73 | 7.6 | 6.1 | N/S | N/S | N/S | 4 | <4 | 1446 | 294 | 2 | 0.4 | 24.77 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-14 | 1.69 | 7.6 | 6.1 | 4 | 4 | N/S | 6 | 4 | 1452 | 300 | 2 | 0.3 | 24.31 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-15 | 1.69 | 7.6 | 5.8 | 3 | 3 | <5 | <4 | <4 | 1482 | 336 | 2 | 0.3 | 25 | 3 | 0.006 | 5 | 1.1 | 24000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-16 | 1.69 | 7.5 | 6.3 | 3 | 2 | N/S | <4 | <4 | 1495 | 336 | 1 | 0.3 | 25.63 | 3 | N/S | N/S | N/S | N/S | 0.05 | 0.047 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.047 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 119 | 39 | 460 | N/S | <8.0 | 5
2013-07-17 | 1.73 | 7.4 | 6.2 | 3 | 3 | N/S | <4 | <4 | 1578 | 444 | 1 | 0.3 | 26.38 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-18 | 1.83 | 7.4 | 6.2 | 4 | 3 | N/S | 6 | <4 | 1479 | 306 | 2 | 0.3 | 25.24 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-19 | 1.88 | 7.2 | 6.7 | N/S | N/S | N/S | 5 | <4 | 1545 | 334 | 2 | 0.2 | 23.95 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-20 | 1.98 | 7.3 | 7 | N/S | N/S | N/S | 7 | 6 | 1749 | 344 | 1 | 0.4 | 22.6 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-21 | 2.14 | 7.3 | 7.1 | 6 | 4 | N/S | 5 | 5 | 1632 | 316 | 1 | 0.2 | 20.14 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-22 | 1.81 | 7.3 | 7.1 | 6 | 4 | <5 | 6 | <4 | 1595 | 350 | 3 | 0.3 | 21.77 | 2.9 | <0.005 | <5 | 1 | 8000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-23 | 1.8 | 7.4 | 6.5 | 8 | 3 | N/S | 8 | 8 | 1497 | 304 | 3 | 0.3 | 23.37 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | <0.005 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.037 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 111 | 40 | 442 | N/S | 8.6 | 5
2013-07-24 | 1.78 | 7.3 | 7.3 | 6 | 4 | N/S | 8 | 6 | 1445 | 308 | 2 | 0.3 | 24.49 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-25 | 1.8 | 7.4 | 6.8 | 5 | 3 | N/S | 5 | 4 | 1288 | 224 | 2 | 0.2 | 24.76 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-26 | 1.8 | 7.3 | 6.8 | N/S | N/S | N/S | <4 | <4 | 1437 | 314 | 2 | 0.2 | 24.93 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-27 | 1.93 | 7.4 | 6.4 | N/S | N/S | N/S | 8 | 7 | 1461 | 350 | 2 | 0.5 | 24.88 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-28 | 1.88 | 7.5 | 6.1 | 4 | 4 | N/S | 4 | <4 | 1582 | 312 | 3 | 0.6 | 24.4 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-29 | 1.81 | 7.4 | 5.6 | 5 | 4 | <5 | <4 | <4 | 1694 | 322 | 3 | 0.4 | 25.01 | 3.5 | <0.005 | 7 | 1.1 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-07-30 | 1.72 | 7.5 | 6.2 | 4 | 3 | N/S | <4 | <4 | 1793 | 354 | 2 | 0.3 | 24.71 | 3.2 | N/S | N/S | N/S | N/S | 0.05 | 0.046 | <0.001 | <0.005 | 0.016 | <0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.033 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 128 | 43 | 498 | N/S | <8.0 | 5
2013-07-31 | 1.8 | 7.5 | 6.3 | 4 | 3 | N/S | 5 | 4 | 1696 | 328 | 2 | 0.2 | 25.69 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-01 | 1.88 | 7.4 | 6.3 | 6 | 5 | N/S | 5 | 4 | 1503 | 252 | 2 | 0.2 | 23.95 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-02 | 2.78 | 7.4 | 6.1 | N/S | N/S | N/S | <4 | <4 | 1276 | 220 | 2 | 0.1 | 16.9 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-03 | 2.24 | 7.4 | 6.2 | N/S | N/S | N/S | 4 | 4 | 1132 | 176 | 2 | <0.1 | 19.74 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-04 | 1.9 | 7.4 | 7.6 | 5 | 3 | N/S | <4 | <4 | 1200 | 186 | 2 | 0.2 | 18.89 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-05 | 1.86 | 7.5 | 7.6 | 5 | 5 | <5 | <4 | <4 | 1170 | 200 | 1 | 0.1 | 20.95 | 2.5 | 0.006 | <5 | 1.1 | 16000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-06 | 1.84 | 7.5 | 7.8 | 4 | 3 | N/S | <4 | <4 | 1062 | 154 | 3 | 0.3 | 21.67 | 2.9 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.018 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 29 | 319 | N/S | 13.5 | 7
2013-08-07 | 1.91 | 7.4 | 7.9 | 6 | 3 | N/S | <4 | <4 | 1033 | 136 | 2 | 0.1 | 22.08 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-08 | 1.82 | 7.4 | 7.4 | 5 | 3 | N/S | 4 | <4 | 1118 | 194 | 2 | 0.2 | 21.72 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-09 | 1.84 | 7.6 | 5.9 | N/S | N/S | N/S | 4 | <4 | 1546 | 338 | 2 | 0.1 | 22.29 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-10 | 1.81 | 7.3 | 8.2 | N/S | N/S | N/S | 4 | <4 | 1748 | 334 | 2 | <0.1 | 22.89 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-11 | 1.69 | 7.4 | 6.4 | 3 | 2 | N/S | <4 | <4 | 1903 | 382 | 1 | <0.1 | 24.21 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-12 | 1.64 | 7.4 | 5.9 | 3 | 3 | <5 | <4 | <4 | 1925 | 392 | 1 | <0.1 | 26.23 | 3 | <0.005 | <5 | 1.2 | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-13 | 1.63 | 7.4 | 6.5 | 3 | 3 | N/S | <4 | <4 | 1868 | 380 | 2 | <0.1 | 26.67 | 3 | N/S | N/S | N/S | N/S | <0.05 | 0.049 | <0.001 | <0.005 | 0.005 | <0.1 | N/S | <0.02 | 0.004 | <0.2 | <0.005 | 0.024 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 131 | 43 | 504 | N/S | <8.0 | 5
2013-08-14 | 1.62 | 7.4 | 6.9 | 3 | 3 | N/S | <4 | <4 | 1816 | 400 | 2 | 0.1 | 27.31 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-15 | 1.7 | 7.4 | 7 | 3 | 3 | N/S | <4 | <4 | 1730 | 356 | 1 | 0.1 | 26.78 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-16 | 1.65 | 7.4 | 7 | N/S | N/S | N/S | 5 | 4 | 1632 | 336 | 1 | <0.1 | 24.93 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-17 | 1.69 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 4 | 1549 | 300 | 1 | <0.1 | 23.89 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-18 | 1.69 | 7.4 | 8 | 3 | 3 | <5 | 5 | 5 | 1530 | 314 | <1 | <0.1 | 24.43 | 3.2 | <0.005 | S/X | S/X | 6000 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X
2013-08-19 | 1.71 | 7.4 | 7.5 | 5 | 4 | T/X | 8 | 7 | 1398 | 274 | 3 | <0.1 | 26.1 | 3.1 | T/X | <5 | 1.2 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-20 | 1.74 | 7.4 | 8 | 6 | 5 | N/S | <4 | <4 | 1363 | 240 | 2 | <0.1 | 25.72 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | <0.005 | <0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.032 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 100 | 33 | 388 | N/S | <8.0 | 6
2013-08-21 | 1.67 | 7.4 | 7.6 | 5 | 3 | N/S | 4 | <4 | 1625 | 376 | 1 | <0.1 | 24.83 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-22 | 2.11 | 7.4 | 7.6 | 6 | 4 | N/S | <4 | <4 | 1870 | 444 | 1 | <0.1 | 23.3 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-23 | 1.78 | 7.4 | 7.6 | N/S | N/S | N/S | 8 | 5 | 1647 | 330 | 1 | <0.1 | 21.11 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-24 | 1.76 | 7.4 | 6.5 | N/S | N/S | N/S | 7 | 6 | 1760 | 346 | 1 | 0.1 | 22.82 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-25 | 1.76 | 7.5 | 6.5 | 8 | 5 | N/S | 8 | 6 | 1871 | 368 | 1 | 0.1 | 23.43 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-26 | 1.69 | 7.4 | 6.3 | 9 | 5 | <5 | 10 | 8 | 1979 | 466 | 1 | 0.1 | 24.34 | 3.2 | <0.005 | 5 | N/R | 4800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-27 | 1.7 | 7.4 | 5.8 | 8 | 4 | N/S | 12 | 7 | 2001 | 550 | 1 | 0.1 | 25.95 | 3.5 | N/S | N/S | N/S | N/S | <0.05 | 0.048 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | 0.039 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 128 | 44 | 502 | N/S | <8.0 | 6
2013-08-28 | 1.67 | 7.3 | 7.2 | 7 | 3 | N/S | 6 | 4 | 1774 | 392 | 1 | 0.1 | 26.45 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-29 | 1.69 | 7.4 | 7 | 6 | 5 | N/S | 8 | 6 | 1651 | 344 | 2 | 0.1 | 26.37 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-30 | 1.33 | 7.5 | 6.1 | N/S | N/S | N/S | 6 | 6 | 1470 | 300 | 2 | 0.2 | 25.79 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-08-31 | 1.95 | 7.4 | 7.7 | N/S | N/S | N/S | 10 | 6 | 1191 | 206 | 4 | 0.3 | 22.09 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-01 | 1.71 | 7.3 | 7.5 | 8 | 6 | N/S | 8 | 8 | 1109 | 162 | 2 | 0.7 | 23.12 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-02 | 1.77 | 7.4 | 7.1 | 9 | 7 | <5 | 8 | 8 | 1152 | 212 | 3 | 0.9 | 24.48 | 3.5 | <0.005 | 7 | 1.1 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-03 | 1.63 | 7.4 | 6.9 | T/X | T/X | N/S | 14 | 13 | 1243 | 242 | 4 | 0.5 | 26.82 | 2.5 | N/S | N/S | N/S | 31000 | <0.05 | 0.036 | <0.001 | <0.005 | 0.017 | 0.1 | <0.1 | <0.02 | 0.014 | <0.2 | <0.005 | 0.034 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 91 | 31 | 357 | N/S | <8.0 | 8
2013-09-04 | 1.57 | 7.3 | 8.3 | 10 | 6 | N/S | 19 | 16 | 1233 | 230 | 4 | 0.4 | 29.14 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-05 | 1.51 | 7.4 | 7 | N/A | 8 | N/S | 18 | 15 | 1304 | 242 | 4 | 0.5 | 30.06 | 4.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-06 | 1.5 | 7.4 | 7.1 | N/S | N/S | N/S | 7 | <4 | 1453 | 296 | 3 | 0.9 | 29.44 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-07 | 1.57 | 7.4 | 6.3 | N/S | N/S | N/S | 7 | 4 | 1550 | 324 | 6 | 3.4 | 24.89 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-08 | 1.57 | 7.5 | 5.2 | 13 | 7 | N/S | 18 | 13 | 1638 | 382 | 6 | 2.4 | 28.31 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-09 | 1.55 | 7.4 | 5.2 | 13 | 8 | <5 | 14 | 13 | 1586 | 360 | 4 | 0.9 | 29.48 | 3.7 | <0.005 | 6 | 1.2 | 42000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-10 | 1.51 | 7.4 | 5.7 | 11 | 6 | N/S | 14 | 11 | 1501 | 318 | 3 | 0.4 | 29.61 | 3.6 | N/S | N/S | N/S | N/S | <0.05 | 0.043 | <0.001 | <0.005 | 0.015 | 0.1 | N/S | <0.02 | 0.02 | <0.2 | <0.005 | 0.043 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 111 | 36 | 428 | N/S | <8.0 | 8
2013-09-11 | 1.52 | 7.3 | 6.5 | 12 | 6 | N/S | 18 | 14 | 1555 | 332 | 2 | 0.4 | 30.96 | 4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-12 | 1.57 | 7.3 | 6.5 | 7 | 5 | N/S | 10 | 9 | 1534 | 322 | 2 | 0.4 | 29.72 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-13 | 1.47 | 7.4 | 7.4 | N/S | N/S | N/S | 18 | 14 | 1482 | 274 | 3 | 0.2 | 28.49 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-14 | 1.58 | 7.4 | 6.9 | N/S | N/S | N/S | 19 | 14 | 1441 | 274 | 2 | 0.3 | 28.59 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-15 | 1.83 | 7.5 | 7 | 14 | 8 | N/S | 18 | 14 | 1469 | 258 | 4 | 0.8 | 26.15 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-16 | 1.79 | 7.3 | 8.1 | 11 | 5 | <5 | 12 | 12 | 1332 | 256 | 3 | 0.4 | 23.86 | 3.2 | <0.005 | 6 | 1.1 | 66000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-17 | 1.73 | 7.3 | 8.3 | 9 | 5 | N/S | 10 | 6 | 1343 | 238 | 4 | 0.4 | 24.35 | 4.3 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.017 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 94 | 34 | 373 | N/S | <8.0 | 7
2013-09-18 | 1.83 | 7.4 | 7.6 | 7 | 5 | N/S | 8 | 6 | 1524 | 246 | 2 | 0.3 | 24.57 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-19 | 1.84 | 7.2 | 8.6 | 7 | 4 | N/S | 7 | 7 | 1372 | 216 | 3 | 0.2 | 23.29 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-20 | 1.69 | 7.2 | 8.4 | N/S | N/S | N/S | 8 | 6 | 1296 | 186 | 2 | 0.1 | 24.34 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-21 | 1.76 | 7.4 | 5.7 | N/S | N/S | N/S | 6 | 6 | 1434 | 244 | 3 | 0.2 | 25.33 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-22 | 1.75 | 7.4 | 6.4 | 8 | 5 | N/S | 7 | 7 | 1653 | 306 | 2 | 0.2 | 25.86 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-23 | 1.63 | 7.4 | 5.9 | 6 | 3 | <5 | 4 | 4 | 1709 | 312 | 2 | 0.2 | 25.9 | 3.4 | <0.005 | <5 | 1.1 | 6300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-24 | 1.61 | 7.5 | 6.3 | 6 | 3 | N/S | 4 | 4 | 1743 | 330 | 2 | 0.1 | 25.84 | 3.3 | N/S | N/S | N/S | N/S | 0.05 | 0.043 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.045 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 119 | 39 | 458 | N/S | <8.0 | 6
2013-09-25 | 1.63 | 7.4 | 6.1 | 5 | 3 | N/S | 5 | 5 | 1745 | 306 | 1 | 0.1 | 26.11 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-26 | 1.6 | 7.4 | 7.5 | 8 | 6 | N/S | 11 | 10 | 1757 | 302 | 1 | <0.1 | 25.63 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-27 | 1.51 | 7.4 | 6.1 | N/S | N/S | N/S | 8 | 4 | 1709 | 310 | 1 | 0.1 | 25.75 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-28 | 1.63 | 7.4 | 7.8 | N/S | N/S | N/S | 5 | <4 | 1659 | 328 | 1 | 0.1 | 25.85 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-29 | 2.12 | 7.4 | 8.6 | 5 | 4 | N/S | 7 | 4 | 1407 | 228 | 2 | 0.1 | 22.94 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-09-30 | 1.64 | 7.3 | 7.4 | 4 | 3 | <5 | 8 | 4 | 1294 | 234 | 1 | 0.1 | 23.81 | 3 | <0.005 | <5 | 1.1 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-01 | 1.62 | 7.4 | 7.8 | 5 | 3 | N/S | 5 | 5 | 1321 | 242 | 2 | 0.1 | 25.79 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.009 | 0.1 | 0.1 | <0.02 | 0.006 | <0.2 | <0.005 | 0.035 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 93 | 32 | 365 | N/S | <8.0 | 6
2013-10-02 | 1.55 | 7.4 | 9 | 4 | 3 | N/S | 4 | 4 | 1400 | 256 | 2 | 0.1 | 27.14 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-03 | 2.09 | 7.4 | 6.1 | T/X | T/X | N/S | 6 | 6 | 1554 | 270 | 1 | <0.1 | 26.16 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-04 | 3.13 | 7.3 | 6.3 | N/S | N/S | N/S | 8 | 6 | 1175 | 172 | 1 | <0.1 | 17 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-05 | 2.38 | 7.4 | 6.4 | N/S | N/S | N/S | 15 | 14 | 1167 | 158 | 1 | <0.1 | 17.05 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-06 | 3.3 | 7.3 | 6.1 | T/X | T/X | N/S | 11 | 10 | 924 | 112 | 2 | <0.1 | 13.52 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-07 | 2.46 | 7.3 | 7.8 | 5 | 3 | <5 | 8 | 5 | 1073 | 160 | 2 | 0.1 | 16.56 | 1.5 | <0.005 | 5 | 0.8 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-08 | 1.85 | 7.3 | 8.6 | 4 | 3 | N/S | 5 | 4 | 1152 | 192 | 2 | 0.1 | 19.91 | 1.8 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.052 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 87 | 30 | 338 | N/S | <8.0 | 6
2013-10-09 | 1.71 | 7.4 | 9.4 | 4 | 3 | N/S | 6 | 4 | 1268 | 202 | 2 | <0.1 | 22.73 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-10 | 1.73 | 7.2 | 7.6 | 5 | 3 | N/S | 7 | 5 | 1262 | 162 | 2 | 0.1 | 24.37 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-11 | 1.67 | 7.2 | 8.1 | N/S | N/S | N/S | 10 | 6 | 1280 | 158 | 2 | <0.1 | 24.94 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-12 | 1.74 | 7.2 | 7.9 | N/S | N/S | N/S | 5 | 4 | 1268 | 160 | 1 | 0.1 | 25.39 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-13 | 1.69 | 7.3 | 7.8 | 4 | 3 | N/S | 7 | 6 | 1305 | 180 | 2 | 0.1 | 25.63 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-14 | 1.64 | 7.4 | 8 | 5 | 3 | <5 | 7 | 6 | 1287 | 186 | 2 | 0.1 | 24.81 | 2.9 | <0.005 | 6 | 1.2 | 800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-15 | 1.72 | 7.4 | 9.5 | 5 | 3 | S/X | 10 | 10 | 1307 | 192 | 2 | 0.1 | 27.02 | 2.9 | S/X | S/X | S/X | S/X | <0.05 | 0.033 | <0.001 | <0.005 | 0.01 | 0.1 | S/X | <0.02 | 0.013 | <0.2 | <0.005 | 0.014 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 89 | 29 | 344 | N/S | <8.0 | 6
2013-10-16 | 1.69 | 7.4 | 8.6 | 6 | 4 | N/S | 10 | 8 | 1295 | 176 | 4 | 0.2 | 25.17 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-17 | 1.92 | 7.4 | 8.7 | 7 | 4 | N/S | 14 | 12 | 1216 | 148 | 2 | 0.2 | 24.48 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-18 | 1.72 | 7.3 | 8.3 | N/S | N/S | N/S | 11 | 10 | 972 | 102 | 2 | 0.2 | 23.63 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-19 | 1.68 | 7.3 | 8.3 | N/S | N/S | N/S | 9 | 8 | 1036 | 96 | 1 | 0.2 | 24.25 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-20 | 1.66 | 7.4 | 8.6 | 10 | 5 | N/S | 9 | 7 | 1196 | 124 | 2 | 0.1 | 23.33 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-21 | 1.73 | 7.3 | 8.5 | 7 | 4 | <5 | 12 | 12 | 1272 | 162 | 3 | 0.3 | 24.81 | 2.9 | <0.005 | <5 | 1.1 | 7200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-22 | 1.8 | 7.4 | 8.4 | 7 | 4 | N/S | 12 | 11 | 1270 | 174 | 2 | 0.1 | 25.54 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.02 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 88 | 30 | 344 | N/S | <8.0 | 6
2013-10-23 | 1.76 | 7.2 | 8.7 | 6 | 3 | N/S | 12 | 10 | 1269 | 196 | 3 | 0.1 | 25.08 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-24 | 1.69 | 7.3 | 8.7 | 6 | 3 | N/S | 8 | 7 | 1271 | 164 | 2 | <0.1 | 25.71 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-25 | 1.62 | 7.4 | 8.6 | N/S | N/S | N/S | 6 | 6 | 1248 | 134 | 3 | 0.1 | 25.53 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-26 | 1.69 | 7.4 | 7.5 | N/S | N/S | N/S | 6 | 5 | 1175 | 118 | 3 | 0.3 | 25.67 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-27 | 1.67 | 7.4 | 7.7 | 6 | 3 | N/S | 4 | <4 | 1106 | 112 | 2 | 0.4 | 25.88 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-28 | 1.57 | 7.3 | 8.4 | 4 | 3 | <5 | <4 | <4 | 1077 | 124 | 1 | 0.2 | 25.96 | 3 | <0.005 | T/X | 1.2 | 1300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-29 | 1.59 | 7.3 | 9.3 | 4 | 3 | N/S | 5 | <4 | 1177 | 192 | 1 | 0.2 | 27.3 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.026 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.003 | <0.2 | <0.005 | 0.019 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 77 | 28 | 306 | N/S | <8.0 | 6
2013-10-30 | 1.86 | 7.4 | 8 | 5 | 3 | N/S | 6 | 5 | 1085 | 182 | 2 | 0.2 | 25.97 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-10-31 | 4.12 | 7.2 | 8.8 | 5 | 3 | N/S | 6 | 6 | 634 | 106 | 1 | <0.1 | 13.41 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-01 | 4.33 | 7.2 | 9 | N/S | N/S | N/S | 6 | 5 | 662 | 76 | 1 | <0.1 | 10 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-02 | 3.85 | 7.2 | 9.3 | N/S | N/S | N/S | 6 | 4 | 896 | 112 | 1 | <0.1 | 11.34 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-03 | 3.12 | 7.3 | 8.9 | 4 | 3 | N/S | <4 | <4 | 1134 | 152 | 1 | 0.3 | 14.68 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-04 | 1.85 | 7.5 | 8.9 | 4 | 2 | <5 | <4 | <4 | 1283 | 176 | 1 | 0.2 | 17.84 | 1.9 | <0.005 | <5 | 0.8 | 1400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-05 | 1.76 | 7.4 | 9 | 5 | 3 | N/S | 6 | 6 | 1283 | 152 | 2 | 0.1 | 20.79 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.01 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.039 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 84 | 30 | 331 | N/S | <8.0 | 6
2013-11-06 | 3.86 | 7.3 | 7.5 | 5 | 4 | N/S | 9 | 7 | 950 | 116 | 1 | <0.1 | 14.59 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-07 | 4.23 | 7.2 | 8.6 | 5 | 3 | N/S | 6 | 4 | 756 | 104 | 1 | <0.1 | 10.35 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-08 | 3.16 | 7.2 | 7.3 | N/S | N/S | N/S | 4 | 4 | 946 | 108 | 1 | 0.1 | 14.12 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-09 | 2.27 | 7.4 | 7.3 | N/S | N/S | N/S | 6 | 4 | 1126 | 130 | 1 | 0.1 | 17.11 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-10 | 2.02 | 7.3 | 7 | 5 | 4 | N/S | 4 | <4 | 1250 | 122 | 1 | 0.2 | 18.06 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-11 | 2.05 | 7.4 | 7.2 | 8 | 5 | <5 | 7 | 6 | 1325 | 152 | 3 | 0.5 | 19.73 | 1.9 | <0.005 | <5 | 1.1 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-12 | 1.95 | 7.4 | 8 | 6 | 4 | N/S | 5 | <4 | 1401 | 166 | 2 | 0.2 | 20.25 | 2 | N/S | N/S | N/S | 2600 | <0.05 | 0.034 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.03 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 87 | 31 | 344 | N/S | <8.0 | 6
2013-11-13 | 1.83 | 7.3 | 8 | 6 | 4 | N/S | 8 | 5 | 1263 | 176 | 1 | 0.1 | 21.16 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-14 | 1.56 | 7.3 | 8.3 | 11 | 6 | N/S | 12 | 10 | 1388 | 160 | 3 | 0.4 | 20.38 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-15 | 1.91 | 7.4 | 8 | N/S | N/S | N/S | 11 | 8 | 1310 | 186 | 3 | <0.1 | 22.45 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-16 | 2.05 | 7.5 | 9.9 | N/S | N/S | N/S | 11 | 9 | 1142 | 164 | 3 | 0.4 | 23.26 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-17 | 2.95 | 7.4 | 9.3 | 10 | 6 | N/S | 10 | 8 | 992 | 138 | 2 | 0.1 | 18.02 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-18 | 3.76 | 7.2 | 8.9 | 13 | 7 | <5 | 20 | 16 | 854 | 130 | 2 | <0.1 | 13 | 1.2 | 0.005 | <5 | 0.6 | 2700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-19 | 3.23 | 7.4 | 10.3 | 7 | 5 | N/S | 8 | 6 | 1006 | 164 | 2 | 0.1 | 15.4 | 1.2 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.012 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 81 | 29 | 324 | N/S | <8.0 | 6
2013-11-20 | 2.1 | 7.5 | 10 | 7 | 5 | N/S | 9 | 8 | 1179 | 162 | 2 | 0.2 | 18.78 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-21 | 2.92 | 7.4 | 9.6 | 10 | 7 | N/S | 8 | 8 | 936 | 130 | 2 | <0.1 | 17.66 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-22 | 2.42 | 7.3 | 8.8 | N/S | N/S | N/S | 9 | 8 | 1123 | 182 | 3 | 0.1 | 17.63 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-23 | 2.27 | 7.4 | 9 | N/S | N/S | N/S | 13 | 8 | 1133 | 164 | 3 | <0.1 | 18.67 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-24 | 2.15 | 7.4 | 9 | 9 | 6 | N/S | 10 | 10 | 1148 | 188 | 3 | 0.1 | 19.53 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-25 | 1.99 | 7.4 | 9.5 | 11 | 7 | <5 | 14 | 11 | 1145 | 136 | 2 | 0.2 | 19.73 | 1.9 | <0.005 | <5 | 0.9 | 1500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-26 | 1.92 | 7.4 | 9.5 | 9 | 6 | N/S | 10 | 9 | 1188 | 172 | 2 | 0.1 | 20.86 | 2.1 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.015 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.03 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 77 | 29 | 311 | N/S | T/X | 7
2013-11-27 | 2.02 | 7.4 | 9.6 | 12 | 8 | N/S | 11 | 9 | 1255 | 146 | 3 | 0.1 | 22 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-28 | 1.99 | 7.4 | 8.3 | 21 | 7 | N/S | 16 | 13 | 1280 | 160 | 4 | 1.1 | 20.28 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-29 | 1.8 | 7.5 | 10.9 | N/S | N/S | N/S | 12 | 10 | 1248 | 182 | 3 | 0.9 | 21.6 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-11-30 | 1.92 | 7.4 | 9.3 | N/S | N/S | N/S | 14 | 11 | 1211 | 198 | 4 | 1.7 | 22.67 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-01 | 1.95 | 7.4 | 10.2 | 19 | 12 | N/S | 14 | 12 | 1252 | 178 | 6 | 3.4 | 20.16 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-02 | 1.64 | 7.4 | 10 | 17 | 10 | <5 | 10 | 9 | 1141 | 144 | 3 | 1 | 22.79 | 2.4 | <0.005 | 5 | T/X | 41000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-03 | 1.61 | 7.4 | 9.8 | 12 | 9 | N/S | 11 | 8 | 1111 | 146 | 2 | 0.3 | 24.63 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.042 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | 0.038 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 79 | 29 | 316 | N/S | <8.0 | 8
2013-12-04 | 1.68 | 7.4 | 8.6 | 14 | 9 | N/S | 9 | 8 | 1107 | 162 | 2 | 0.3 | 25.17 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-05 | 1.65 | 7.3 | 7.2 | 20 | 10 | N/S | 17 | 13 | 1156 | 148 | 3 | 0.2 | 27.79 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-06 | 1.67 | 7.3 | 9 | N/S | N/S | N/S | 13 | 10 | 1144 | 130 | 3 | 0.1 | 27.89 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-07 | 1.81 | 7.4 | 8.5 | N/S | N/S | N/S | 13 | 11 | 1140 | 142 | 2 | 0.2 | 27.32 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-08 | 1.82 | 7.4 | 10 | 11 | 7 | N/S | 10 | 8 | 1143 | 128 | 2 | 0.5 | 26.15 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-09 | 1.7 | 7.3 | 9.3 | 10 | 5 | <5 | 9 | 9 | 1184 | 158 | 2 | 0.2 | 26.51 | 3.2 | 0.005 | <5 | 1.1 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-10 | 1.7 | 7.2 | 10 | 9 | 5 | N/S | 8 | 8 | 1210 | 158 | 3 | 0.1 | 27.26 | 3.6 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.028 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 82 | 30 | 326 | N/S | <8.0 | 7
2013-12-11 | 1.7 | 7.3 | 10 | 9 | 5 | N/S | 10 | 9 | 1216 | 158 | 3 | 0.1 | 27.64 | 4.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-12 | 1.71 | 7.4 | 10.9 | 9 | 6 | N/S | 10 | 6 | 1240 | 144 | 2 | 0.2 | 27.18 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-13 | 1.68 | 7.5 | 10 | N/S | N/S | N/S | 14 | 10 | 1295 | 206 | 3 | 0.1 | 27.34 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-14 | 1.82 | 7.4 | 9.6 | N/S | N/S | N/S | 13 | 12 | 1528 | 232 | 3 | 0.4 | 25.47 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-15 | 1.69 | 7.4 | 9.9 | 20 | 13 | N/S | 29 | 24 | 1714 | 206 | 4 | 0.6 | 23.9 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-16 | 1.5 | 7.3 | 9.8 | 27 | 13 | <5 | 33 | 25 | 1569 | 204 | 5 | 0.2 | 24.42 | 3.2 | 0.005 | 5 | 1.1 | 5600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-17 | 1.49 | 7.3 | 10 | 23 | 10 | N/S | 32 | 25 | 1587 | 232 | 3 | 0.1 | 25.96 | 3.4 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.033 | 0.2 | N/S | <0.02 | 0.03 | <0.2 | <0.005 | 0.031 | <0.001 | 0.06 | <0.05 | <0.001 | <0.1 | <6 | 100 | 34 | 389 | N/S | <8.0 | 7
2013-12-18 | 1.51 | 7.4 | 10 | 11 | 11 | N/S | 10 | 8 | 1612 | 224 | 3 | 0.3 | 26.58 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-19 | 1.57 | 7.4 | 4 | 12 | 6 | N/S | 10 | 6 | 1474 | 142 | 3 | 0.8 | 26.42 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-20 | 2.51 | 7.3 | 9.1 | N/S | N/S | N/S | 13 | 8 | T/X | T/X | 2 | 0.5 | 20.42 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-21 | 2.85 | 7.3 | 9 | N/S | N/S | N/S | 12 | 9 | T/X | T/X | 2 | 0.2 | 16.49 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-22 | 3.76 | 7.2 | 10.5 | 11 | 7 | N/S | 18 | 13 | T/X | T/X | 2 | 0.2 | 13.29 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-23 | 3.24 | 7.2 | 10.3 | 12 | 8 | <5 | 14 | 9 | T/X | T/X | 2 | 0.2 | 13.95 | 1.3 | 0.005 | <5 | 0.6 | 21000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-24 | 2.84 | 7.2 | 8.2 | 17 | 9 | N/S | 8 | 6 | T/X | T/X | 3 | 1 | 14.79 | 1.7 | N/S | N/S | N/S | N/S | 0.06 | 0.056 | <0.001 | <0.005 | 0.031 | 0.2 | N/S | <0.02 | 0.023 | <0.2 | <0.005 | 0.03 | <0.001 | 0.06 | <0.05 | <0.001 | <0.1 | <6 | 96 | 36 | 387 | N/S | <8.0 | 6
2013-12-25 | 1.97 | 7.3 | 8.5 | 11 | 8 | N/S | 10 | 8 | T/X | T/X | 3 | 1 | 16.99 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-26 | 1.86 | 7.3 | 10.6 | 9 | 4 | N/S | 10 | 5 | T/X | T/X | 4 | 0.8 | 19.54 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-27 | 1.78 | 7.5 | 9.1 | N/S | N/S | N/S | 8 | 5 | T/X | T/X | 4 | 2.2 | 19.42 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-28 | 1.87 | 7.4 | 10.3 | N/S | N/S | N/S | 34 | 27 | T/X | T/X | 4 | 1 | 19.66 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-29 | 1.85 | 7.4 | 9 | 15 | 8 | N/S | 7 | 7 | T/X | T/X | 5 | 1.6 | 19.3 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-30 | 1.73 | 7.4 | 10 | 12 | 8 | <5 | 7 | 6 | T/X | T/X | 3 | 0.9 | 21.24 | 2.8 | 0.005 | 6 | 0.8 | 800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2013-12-31 | 1.7 | 7.5 | 10.5 | 14 | 8 | N/S | 13 | 11 | T/X | T/X | 3 | 0.5 | 22.34 | 2.6 | N/S | N/S | N/S | N/S | 0.06 | 0.043 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.02 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 99 | 35 | 392 | N/S | <8.0 | 6
Reporting Limit (RL) |  |  |  | 2 | 2 | 5 | 4 | 4 | 100 |  | 1 | 0.1 | 0.15 | 0.2 | 0.005 | 5 | 0.1 |  | 0.05 | 0.004 | 0.001 | 0.005 | 0.005 | 0.1 | 0.1 | 0.02 | 0.001 | 0.2 | 0.005 | 0.005 | 0.001 | 0.01 | 0.05 | 0.001 | 0.1 | 6 | 1 | 1 |  |  | 0.5 | 1
Observations | 365 | 365 | 365 | 255 | 254 | 50 | 365 | 365 | 353 | 353 | 365 | 365 | 365 | 362 | 52 | 51 | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 12 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 0 | 52 | 53
Minimum | 1.33 | 7 | 4 | 3 | 2 | <5 | <4 | <4 | 502 | 76 | <1 | <0.1 | 5.92 | 0.5 | <0.005 | <5 | 0.3 | 800 | <0.05 | 0.026 | <0.001 | <0.005 | <0.005 | <0.1 | <0.1 | <0.02 | 0.003 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 71 | 28 | 291 |  | <5.0 | 4
Mean | 2.24 | 7.4 | 7.9 | 9 | 5 | <5 | <9 | <7 | 1267 | 204 | <3 | <0.4 | 20.05 | 2.5 | <0.006 | <6 | 0.9 | 16998 | <0.05 | 0.037 | <0.001 | <0.005 | <0.012 | <0.1 | <0.1 | <0.02 | 0.01 | <0.2 | <0.005 | <0.030 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 91 | 33 | 365 |  | <8.2 | 6
Maximum | 4.5 | 7.7 | 12.2 | 27 | 15 | 6 | 34 | 27 | 2489 | 550 | 6 | 3.4 | 30.96 | 4.3 | 0.014 | 14 | 1.2 | 240000 | 0.08 | 0.056 | <0.001 | <0.005 | 0.042 | 0.2 | 0.1 | <0.02 | 0.03 | <0.2 | <0.005 | 0.066 | 0.001 | 0.06 | <0.05 | <0.001 | <0.1 | <6 | 131 | 44 | 504 |  | 13.5 | 8
Std Dev | 0.77 | 0.1 | 1.2 | 4 | 2 | 0 | 5 | 4 | 297 | 74 | 1 | 0.5 | 5.02 | 0.8 | 0.002 | 1 | 0.2 | 34474 | 0 | 0.006 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0.011 | 0 | 0.01 | 0 | 0 | 0 | 0 | 14 | 4 | 52 |  | 1 | 1
* LL Hg: Based on the sample matrix some samples need to be diluted. The reporting limit
of 0.5 ng/L for LL Hg will then change by the same factor.
January 2 and 31, 2013 BOD5: Batch failed QA standard; analysis exempt from rerun.
January 2 and 31, 2013 CBOD5, T/X: Batch failed QA standard.
January 7-8, 2013 P Tot, T/X: QA failure.
January 14, 2013 FOG, T/X: QA failure.
February 3, 2013 BOD5, N/A: DO did not meet acceptance criteria.
February 12, 2013 Hg: Aliquot not preserved; added prior to analysis.
April 4, 2013 BOD5: Batch failed QA standard; analysis exempt from rerun.
April 4, 2013 CBOD5, T/X: Batch LCS failure.
April 16, 2013 NO2 +NO3_N: Sample MS recovery failed but LCS passed.
June 16, 2013 NO2=NO3_N: Sample MS recovery failed but LCS passed.
June 23, 2013 BOD5, CBOD5, T/X: Batch LCS failure.
August 26, 2013 F, N/R: Sample never arrived at laboratory.
September 3, 2013 BOD5, CBOD5 T/X: Batch LCS failure.
September 5, 2013 BOD5 N/A: Dilutions for BOD did not meet the minimum O2 loss of at least 2 mg/L.
September 19, 2013 TKN: Spike failed recovery, LCS passed.
September 28, 2013 Tot Phos: Spike failed recovery, LCS passed.
October 2, 8 and 20, 2013 Tot Phos: Spike failed recovery, LCS passed.
October 5, 2013 BOD5, CBOD5 T/X: Batch LCS failure.
October 5 and 25, 2013 Tot NO2+NO3: Spike failed recovery, LCS passed.
October 28, 2013 Phenol T/X: Blank analyzed instead of sample.
November 5, 6 and 10, 2013 Tot Phos: Spike failed recovery, LCS passed.
November 6, 10, 17 and 30, 2013 Tot NO2+NO3: Spike failed recovery, LCS passed.
November 26, 2013 LL Hg, T/X: Sample never arrived at the laboratory.
December 3 . 2013 Hg: Aliquot not preserved' added prior to analysis.
December 9, 2013 TKN: Sample MS recovery failed but LCS passed.
December 10, 2013 Tot Phos: Spike failed recovery, LCS passed.
December 20-31 TS, TVS, T/X: Insufficient sample volume for analysis.
December 24, 2013 Hg: Sample MS recovery failed but LCS passed.
December 25, 2013 Tot NO2+NO3: Spike failed recovery, LCS passed.
December 31, 2013 BOD5, CBOD5: Incubation period of 6 days.

## Lemont Outfall 2014
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2014-01-01 | 1.69 | 7.3 | 9.5 | 6 | 8 | N/S | 12 | 11 | T/X | T/X | 4 | 1 | 23.16 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-02 | 1.65 | 7.4 | 9.5 | 4 | 7 | N/S | 10 | 8 | T/X | T/X | 4 | 0.8 | 24.19 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-03 | 1.67 | 7.4 | 11 | N/S | N/S | N/S | 12 | 10 | T/X | T/X | 3 | 0.5 | 25.01 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-04 | 1.76 | 7.3 | 9.3 | N/S | N/S | N/S | 8 | 8 | 1554 | 182 | 4 | 1 | 23.72 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-05 | 1.72 | 7.3 | 10.7 | 11 | 9 | N/S | 12 | 10 | 1636 | 208 | 3 | 1.3 | 25.97 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-06 | 1.75 | 7.2 | 10.7 | 12 | 9 | <5 | 11 | 11 | 1561 | 160 | 4 | 0.9 | 26.18 | 3 | 0.006 | 5 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-07 | 1.69 | 7.2 | 10.8 | 10 | 7 | N/S | 10 | 10 | 1381 | 126 | 2 | 0.3 | 24.84 | 2.7 | N/S | N/S | N/S | N/S | 0.06 | 0.039 | <0.001 | <0.005 | 0.021 | 0.1 | <0.1 | <0.02 | 0.01 | <0.2 | <0.005 | 0.032 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | N/S | 90 | 30 | 349 | <8.0 | 6
2014-01-08 | 1.61 | 7.5 | 11.6 | 8 | 5 | N/S | 10 | 7 | 1305 | 154 | 2 | 0.3 | 25.2 | 2.6 | N/S | N/S | N/S | 4600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-09 | 1.62 | 7.3 | 10.2 | 9 | 5 | N/S | 8 | 8 | 1250 | 178 | 2 | 0.3 | 25.26 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2014-01-10 | 1.95 | 7.3 | 10 | N/S | N/S | N/S | 32 | 25 | 1402 | 150 | 4 | 0.2 | 24.36 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-11 | 4.25 | 7.1 | 10 | N/S | N/S | N/S | 14 | 11 | 1568 | 178 | 2 | 0.1 | 12.37 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-12 | 4.25 | 7.1 | 9.8 | 11 | 9 | N/S | 17 | 15 | 1578 | 174 | 2 | 0.1 | 12.01 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-13 | 4.5 | 7.2 | 9.6 | 18 | 13 | <5 | 23 | 21 | 1754 | 220 | 2 | 0.3 | 12.09 | 1.3 | 0.007 | 10 | 0.5 | 18000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-14 | 4.59 | 7.3 | 10 | 8 | 6 | N/S | 9 | 9 | 1733 | 212 | 1 | 0.1 | 11.1 | 0.9 | N/S | N/S | N/S | N/S | 0.05 | 0.047 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.04 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 93 | 35 | 374 | 21.9 | 4
2014-01-15 | 3.43 | 7.2 | 7.5 | 8 | 6 | N/S | 8 | 7 | 1479 | 154 | 1 | 0.1 | 12.05 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-16 | 2.87 | 7.3 | 8.8 | 6 | 4 | N/S | 7 | 7 | 1457 | 206 | 2 | 0.2 | 14.45 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-17 | 2.12 | 7.4 | 10 | N/S | N/S | N/S | 8 | 8 | 1431 | 174 | 2 | 0.2 | 16.58 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-18 | 2.08 | 7.3 | 9.4 | N/S | N/S | N/S | 9 | 8 | 1313 | 140 | 3 | 0.4 | 17.88 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-19 | 2.03 | 7.4 | 10 | 7 | 4 | N/S | 7 | 6 | 1452 | 160 | 2 | 0.8 | 17.51 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-20 | 1.99 | 7.3 | 8.4 | 7 | 4 | <5 | 8 | 6 | 1640 | 180 | 2 | 0.5 | 18.32 | 2.3 | 0.005 | <5 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-21 | 1.84 | 7.3 | 8.3 | 5 | 4 | N/S | 5 | 4 | 1665 | 178 | 2 | 0.3 | 19.4 | 2.5 | N/S | N/S | N/S | 1300 | 0.06 | 0.048 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.035 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 102 | 38 | 414 | <8.0 | 6
2014-01-22 | 1.79 | 7.3 | 9.4 | 7 | 4 | N/S | 9 | 9 | 1617 | 216 | 2 | 0.3 | 21.27 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-23 | 1.82 | 7.3 | 10 | T/X | T/X | N/S | 8 | 6 | 1516 | 166 | 2 | 0.2 | 22.89 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-24 | 1.8 | 7.3 | 9.7 | N/S | N/S | N/S | 9 | 9 | 1377 | 228 | 2 | 0.2 | 20.65 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-25 | 1.85 | 7.4 | 11.2 | N/S | N/S | N/S | 12 | 12 | 1394 | 172 | 3 | 0.7 | 20.59 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-26 | 1.8 | 7.4 | 11.1 | T/X | T/X | N/S | 11 | 10 | 1345 | 160 | 3 | 1.1 | 20.69 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-27 | 1.74 | 7.3 | 10.9 | T/X | T/X | 19 | 12 | 11 | 1286 | 180 | 2 | 0.5 | 21.72 | 3 | 0.006 | 12 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-28 | 1.77 | 7.4 | 11.4 | 7 | 5 | N/S | 7 | 7 | 1178 | 108 | 3 | 0.2 | 21.97 | 3.4 | N/S | N/S | N/S | 7800 | 0.06 | 0.032 | <0.001 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.017 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 77 | 29 | 312 | <8.0 | 7
2014-01-29 | 1.7 | 7.3 | 7.4 | 7 | 5 | N/S | 8 | 6 | 1170 | 128 | 2 | 0.2 | 21.94 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-30 | 1.65 | 7.3 | 10 | 9 | 5 | N/S | 6 | 6 | 1190 | 136 | 2 | 0.2 | 22.5 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-01-31 | 1.61 | 7.2 | 10 | N/S | N/S | N/S | 6 | <4 | 1158 | 172 | 3 | 0.2 | 23.47 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-01 | 1.75 | 7.2 | 9.6 | N/S | N/S | N/S | 10 | 6 | 1156 | 150 | 4 | 1.4 | 22.82 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-02 | 1.76 | 7.2 | 8.4 | 10 | 7 | N/S | 4 | 4 | 1126 | 156 | 5 | 1.9 | 20.99 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-03 | 1.69 | 7.3 | 8.1 | 12 | 7 | <5 | 6 | 6 | 1155 | 124 | 6 | 1.3 | 21.17 | 6 | 0.006 | 8 | 1.1 | 30000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-04 | 1.56 | 7.3 | 8 | 11 | 6 | N/S | 7 | 4 | 1123 | 114 | 3 | 0.5 | 22.4 | 2.6 | N/S | N/S | N/S | N/S | 0.05 | 0.031 | <0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.01 | <0.2 | <0.005 | 0.052 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 29 | 319 | <8.0 | 8
2014-02-05 | 1.57 | 7.3 | 8.4 | 11 | 7 | N/S | 8 | 7 | 1178 | 148 | 4 | 0.3 | 24.15 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-06 | 1.59 | 7.3 | 10.4 | 9 | 6 | N/S | 6 | 6 | 1273 | 184 | 3 | 0.2 | 26.07 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-07 | 1.59 | 7.3 | 10.4 | N/S | N/S | N/S | 8 | 7 | 1205 | 188 | 3 | 0.2 | 26.58 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-08 | 1.66 | 7.3 | 10.6 | N/S | N/S | N/S | 9 | 6 | 1162 | 160 | 3 | 0.4 | 26.13 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-09 | 1.7 | 7.3 | 10.6 | 12 | 8 | N/S | 7 | 6 | 1076 | 144 | 4 | 0.6 | 24.72 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-10 | 1.59 | 7.4 | 10 | 7 | 6 | <5 | 6 | 4 | 1181 | 114 | <1 | 0.3 | 24.97 | 3.6 | <0.005 | <5 | 1.1 | 21000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-11 | 1.58 | 7.4 | 11 | 8 | 6 | N/S | 5 | 4 | 1226 | 162 | <1 | 0.3 | 25.73 | 3.3 | N/S | N/S | N/S | N/S | 0.05 | 0.036 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.031 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 89 | 29 | 344 | <8.0 | 8
2014-02-12 | 1.58 | 7.2 | 10.3 | 9 | 6 | N/S | 6 | 6 | 1187 | 146 | 3 | 0.2 | 25.55 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-13 | 1.58 | 7.3 | 10.3 | 8 | 6 | N/S | 7 | 5 | 1193 | 174 | 3 | 0.3 | 25.54 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-14 | 1.55 | 7.4 | 11.4 | N/S | N/S | N/S | <4 | <4 | 1174 | 208 | 2 | 0.3 | 25.26 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-15 | 1.65 | N/S | 10 | N/S | N/S | N/S | 6 | 4 | 1058 | 154 | 2 | 0.5 | 24.19 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-16 | 1.6 | N/S | 10 | 8 | 6 | N/S | 7 | 5 | 1036 | 162 | 2 | 0.4 | 23.54 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-17 | 1.54 | N/S | 9.8 | 7 | 5 | <5 | 5 | <4 | 1033 | 120 | 2 | 0.2 | 23.76 | 2.9 | <0.005 | 6 | 1.1 | 28000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-18 | 1.79 | N/S | 10 | 7 | 5 | N/S | 4 | <4 | 1122 | 110 | 2 | 0.2 | 23.38 | 2.8 | N/S | N/S | N/S | N/S | 0.05 | 0.03 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.026 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 74 | 26 | 290 | <8.0 | 7
2014-02-19 | 2.17 | 7.3 | 9.6 | 7 | 5 | N/S | 5 | 4 | 1570 | 144 | 2 | 0.2 | 19.61 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-20 | 2.87 | 7 | 11.7 | 6 | 4 | N/S | 5 | 5 | 1662 | 174 | 2 | 0.2 | 13.65 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-21 | 3.1 | 7 | 13 | N/S | N/S | N/S | 5 | 5 | 1280 | 144 | 1 | 0.1 | 8.97 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-22 | 3.03 | 7 | 10.6 | N/S | N/S | N/S | <4 | <4 | 1367 | 154 | <1 | 0.1 | 10.72 | 0.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-23 | 2.95 | 7 | 11.5 | 5 | 3 | N/S | 5 | <4 | 1414 | 162 | 2 | 0.1 | 13.12 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-24 | 2.8 | 7 | 12.2 | 6 | 3 | <5 | <4 | <4 | 1359 | 144 | 2 | 0.4 | 13.61 | 1.2 | 0.005 | 6 | 0.7 | 40000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-25 | 2.8 | 7.3 | 10.8 | 6 | 3 | N/S | <4 | <4 | 1398 | 180 | 2 | 0.4 | 13.97 | 1.5 | N/S | N/S | N/S | N/S | 0.06 | 0.044 | <0.001 | <0.005 | 0.005 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.039 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 94 | 34 | 375 | <8.0 | 5
2014-02-26 | 2.62 | 7.4 | 10 | 9 | 4 | N/S | <4 | <4 | 1458 | 188 | 3 | 1.8 | 16.17 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-02-27 | 2.07 | 7.5 | 10.7 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | N/S | S/X
2014-02-28 | 1.81 | 7.7 | 10.3 | N/S | N/S | N/S | 6 | 4 | 1471 | 226 | 2 | 0.4 | 19.85 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-01 | 1.84 | 7.4 | 11.3 | N/S | N/S | N/S | <4 | <4 | 1418 | 194 | 4 | 1.4 | 19.6 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-02 | 1.82 | 7.5 | 9.4 | T/X | T/X | N/S | 4 | 4 | 1410 | 178 | 4 | 1.9 | 19.55 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-03 | 1.76 | 7.4 | 9.5 | 8 | 5 | <5 | <4 | <4 | 1416 | 148 | 3 | 1 | 20.51 | 2.3 | 0.005 | 7 | 1 | 18000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-04 | 1.7 | 7.4 | 8.9 | 6 | 3 | N/S | <4 | <4 | 1416 | 150 | 2 | 0.2 | 21.18 | 2.3 | N/S | N/S | N/S | N/S | 0.07 | 0.042 | <0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.006 | <0.2 | <0.005 | 0.085 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 94 | 33 | 370 | 312 | 6
2014-03-05 | 1.66 | 7.4 | 10.6 | 7 | 5 | N/S | <4 | <4 | 1417 | 168 | 2 | 0.3 | 22.65 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-06 | 1.75 | 7.5 | 9.9 | 9 | 5 | N/S | 7 | 7 | 1460 | 176 | 3 | 0.4 | 21.93 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-07 | 1.93 | 7.5 | 8 | N/S | N/S | N/S | 8 | 7 | 1550 | 230 | <1 | 0.6 | 20 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-08 | 1.96 | 7.4 | 10.3 | N/S | N/S | N/S | 8 | 8 | 1509 | 184 | <1 | 0.5 | 19.06 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-09 | 2.08 | 7.4 | 9.2 | T/X | T/X | N/S | 8 | 6 | 1388 | 158 | <1 | 1.1 | 18.07 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-10 | 2.6 | 7.3 | 8.4 | 9 | 6 | <5 | 7 | 7 | 1406 | 146 | 3 | 0.5 | 15.63 | 2 | 0.005 | <5 | 0.8 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-11 | 4.32 | 7.2 | 9.9 | T/X | T/X | N/S | 8 | 8 | 1325 | 108 | 2 | 0.3 | 11.34 | 1.2 | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 75 | 29 | 306 | <8.0 | 5
2014-03-12 | 4.32 | 7.3 | 10 | 10 | 7 | N/S | 8 | 7 | 1333 | 148 | 2 | 0.2 | 9.08 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-13 | 4.18 | 7.3 | 9.8 | 13 | 8 | N/S | 10 | 9 | 1464 | 148 | 2 | 0.4 | 9.72 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-14 | 4.11 | 7.2 | 10 | N/S | N/S | N/S | 11 | 8 | 1374 | 178 | 2 | 0.5 | 9.74 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-15 | 4.1 | 7.3 | 8.6 | N/S | N/S | N/S | 10 | 8 | 1081 | 142 | 2 | 0.1 | 8.07 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-16 | 4.08 | 7.2 | 9.9 | 9 | 6 | N/S | 8 | 7 | 1195 | 152 | 2 | 0.3 | 9.61 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-17 | 4.05 | 7.3 | 8 | 13 | 7 | <5 | 8 | 8 | 1166 | 128 | 3 | 0.7 | 10.49 | 1 | <0.005 | <5 | 0.5 | 9200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-18 | 3.32 | 7.4 | 7.8 | 11 | 7 | N/S | 10 | 8 | 1202 | 154 | 2 | 0.5 | 11.68 | 1.2 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.019 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 82 | 33 | 340 | <8.0 | 6
2014-03-19 | 4.15 | 7.3 | 8.7 | 8 | 6 | N/S | 10 | 7 | 1046 | 112 | 2 | 0.1 | 10.19 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-20 | 4.42 | 7.4 | 10 | 6 | 5 | N/S | 8 | 6 | 978 | 68 | 2 | 0.2 | 9.47 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-21 | 4.23 | 7.3 | 9.8 | N/S | N/S | N/S | 13 | 12 | 1168 | 164 | 2 | 0.1 | 11.73 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-22 | 4.22 | 7.3 | 10 | N/S | N/S | N/S | 11 | 9 | 1089 | 134 | 2 | 0.2 | 12.16 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-23 | 2.94 | 7.3 | 10.7 | T/X | T/X | N/S | 6 | 6 | 1107 | 134 | 2 | 0.1 | 13.11 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-24 | 2.67 | 7.3 | 10.6 | 11 | 7 | <5 | 11 | 10 | 1069 | 150 | 2 | 0.2 | 16.31 | 1.4 | 0.008 | 5 | T/X | 2100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-25 | 2.98 | 7.3 | 10.3 | 18 | 9 | N/S | 14 | 11 | 1140 | 142 | 3 | 1 | 16.45 | 1.7 | N/S | N/S | N/S | N/S | 0.05 | 0.037 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 36 | 367 | <8.0 | 6
2014-03-26 | 2.24 | 7.5 | 9.7 | 30 | 16 | N/S | 38 | 30 | 1294 | 272 | 6 | 0.8 | 15.17 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-27 | 2.5 | 7.4 | 10 | 10 | 8 | N/S | 9 | 8 | 1359 | 230 | 3 | 0.2 | 18.16 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-28 | 2.44 | 7.4 | 9.2 | N/S | N/S | N/S | 10 | 9 | 1469 | 248 | 3 | 0.1 | 17.18 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-29 | 2.29 | 7.3 | 8 | N/S | N/S | N/S | 10 | 8 | 1396 | 214 | 3 | 0.1 | 17.37 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-30 | 2.28 | 7.4 | 9.4 | 9 | 8 | N/S | 10 | 8 | 1401 | 194 | 3 | 0.1 | 17.48 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-03-31 | 2.18 | 7.4 | 8.4 | 12 | 6 | <5 | 7 | 5 | 1416 | 244 | 3 | 0.2 | 17.53 | 1.8 | 0.006 | <5 | 0.8 | 25000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-01 | 2.29 | 7.4 | 8.4 | 12 | 7 | N/S | 10 | 8 | 1467 | 258 | 3 | 0.3 | 17.94 | 2 | N/S | N/S | N/S | N/S | 0.06 | 0.045 | <0.001 | <0.005 | 0.011 | 0.1 | <0.1 | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 102 | 40 | 420 | T/X | 7
2014-04-02 | 1.96 | 7.4 | 7.8 | 15 | 6 | N/S | 9 | 8 | 1500 | 284 | 3 | 0.2 | 18.24 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-03 | 3.59 | 7.4 | 9.6 | 10 | 6 | N/S | 12 | 9 | 1069 | 156 | 2 | 0.1 | 12.45 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-04 | 4.25 | 7.4 | 10 | N/S | N/S | N/S | 10 | 9 | 994 | 200 | 2 | 0.1 | 8.77 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-05 | 4.25 | 7.4 | 10.8 | N/S | N/S | N/S | 10 | 10 | 1077 | 182 | 2 | 0.2 | 10.61 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-06 | 2.93 | 7.4 | 10.5 | 9 | 5 | N/S | 12 | 11 | 1145 | 194 | 2 | 0.3 | 11.56 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-07 | 2.47 | 7.4 | 10 | 11 | 6 | <5 | 9 | 6 | 1140 | 156 | 3 | 0.5 | 13.04 | 1.1 | <0.005 | 6 | 0.7 | 27000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-08 | 3.25 | 7.5 | 9.1 | 18 | 7 | N/S | 10 | 6 | 1029 | 96 | 4 | 2.3 | 12.78 | 1.3 | N/S | N/S | N/S | N/S | 0.05 | 0.037 | <0.001 | <0.005 | 0.027 | 0.1 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.037 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 84 | 35 | 355 | <8.0 | 7
2014-04-09 | 2.16 | 7.5 | 10 | 9 | 5 | N/S | 6 | 5 | 1017 | 134 | 2 | 0.7 | 15.3 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-10 | 2.08 | 7.4 | 8.1 | 9 | 5 | N/S | 7 | <4 | 1109 | 202 | 2 | 0.5 | 17.96 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-11 | 2.24 | 7.5 | 7.2 | N/S | N/S | N/S | 4 | 4 | 1060 | 166 | 2 | 0.3 | 18.48 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-12 | 2.33 | 7.4 | 10 | N/S | N/S | N/S | 6 | 5 | 1023 | 162 | 3 | 0.4 | 19.18 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-13 | 2.42 | 7.3 | 8.8 | 9 | 5 | N/S | <4 | <4 | 1008 | 138 | 3 | 0.7 | 17.86 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-14 | 2.91 | 7.3 | 7.8 | 11 | 7 | <5 | 9 | 8 | 980 | 168 | 3 | 0.3 | 16.95 | 2.1 | <0.005 | 6 | 0.7 | 3200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-15 | 3.17 | 7.2 | 8.3 | 9 | 5 | N/S | 8 | 6 | 1042 | 150 | 2 | 0.4 | 15.11 | 1.8 | N/S | N/S | N/S | N/S | 0.05 | 0.034 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | 0.032 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 85 | 34 | 354 | <8.0 | 7
2014-04-16 | 2.74 | 7.3 | 9.8 | 10 | 5 | N/S | 10 | 9 | 1109 | 232 | 2 | 0.4 | 17.76 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-17 | 2.29 | 7.4 | 9 | 10 | 6 | N/S | 12 | 8 | 1173 | 192 | 3 | 0.1 | 18.96 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-18 | 2.12 | 7.3 | 8.3 | N/S | N/S | N/S | 16 | 10 | 1253 | 262 | 3 | 0.5 | 19.57 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-19 | 2.47 | 7.4 | 8.6 | N/S | N/S | N/S | 21 | 15 | 1273 | 218 | 4 | 1.2 | 18.7 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-20 | 2.2 | 7.5 | 10 | 24 | 12 | N/S | 27 | 22 | 1260 | 212 | 5 | 1.6 | 17.78 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-21 | 2 | 7.5 | 8.4 | 20 | 10 | 5 | 23 | 20 | 1287 | 240 | 5 | 1 | 19.03 | 3.1 | 0.007 | 7 | 1 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-22 | 2.37 | 7.3 | 8.8 | 18 | 10 | N/S | 20 | 18 | 1278 | 248 | 5 | 0.7 | 18.17 | 2.8 | N/S | N/S | N/S | N/S | 0.05 | 0.038 | <0.001 | <0.005 | 0.023 | 0.2 | N/S | <0.02 | 0.027 | <0.2 | <0.005 | 0.041 | <0.001 | 0.06 | <0.05 | <0.001 | <0.1 | <6 | 90 | 35 | 367 | <8.0 | 10
2014-04-23 | 2.25 | 7.4 | 8.2 | 20 | 8 | N/S | 17 | 15 | 1238 | 196 | 5 | 1.6 | 18.66 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-24 | 2.01 | 7.5 | 8 | 19 | 7 | N/S | 16 | 13 | 1332 | 258 | 4 | 0.8 | 20.34 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-25 | 2.41 | 7.3 | 9.5 | N/S | N/S | N/S | 10 | 7 | 1277 | 314 | 4 | 0.6 | 19.64 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-26 | 2.17 | 7.3 | 8.8 | N/S | N/S | N/S | 13 | 10 | 1283 | 304 | 4 | 0.6 | 20.2 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-27 | 2.18 | 7.3 | 8.7 | 23 | 9 | N/S | 17 | 14 | 1223 | 264 | 5 | 1.3 | 20.81 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-28 | 2.99 | 7.3 | 8.2 | 20 | 8 | <5 | 20 | 17 | 1132 | 232 | 3 | 0.7 | 17.84 | 2.6 | 0.007 | 7 | 0.8 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-04-29 | 3.16 | 7.3 | 7.6 | T/X | T/X | N/S | 16 | 14 | 1030 | 280 | 3 | 0.3 | 15.86 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.011 | 0.2 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | 0.032 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 78 | 30 | 321 | <8.0 | 8
2014-04-30 | 2.47 | 7.4 | 9.7 | 11 | 6 | N/S | 12 | 9 | 1171 | 198 | 2 | 0.3 | 16.81 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-01 | 2.27 | 7.5 | 10.4 | 13 | 6 | N/S | 12 | 10 | 1295 | 224 | 3 | 0.3 | 19.98 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-02 | 2.27 | 7.5 | 9.7 | N/S | N/S | N/S | 11 | 11 | 1363 | 240 | 3 | 0.2 | 19.75 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-03 | 2.32 | 7.4 | 9.8 | N/S | N/S | N/S | 11 | 11 | 1336 | 224 | 3 | 0.5 | 19.74 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-04 | 2.15 | 7.4 | 9.3 | 13 | 6 | N/S | 8 | 6 | 1302 | 194 | 3 | 0.7 | 20 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-05 | 2.01 | 7.5 | 10.7 | 9 | 5 | <5 | 5 | 5 | 1331 | 260 | 3 | 0.4 | 22.68 | 3 | 0.007 | <5 | 0.9 | 5300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-06 | 1.98 | 7.3 | 10.7 | 8 | 5 | N/S | 6 | 5 | 1314 | 276 | 2 | 0.2 | 23.84 | 3.1 | N/S | N/S | N/S | N/S | 0.05 | 0.036 | <0.001 | <0.005 | 0.007 | 0.1 | <0.1 | <0.02 | 0.009 | <0.2 | <0.005 | 0.024 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 34 | 357 | <8.0 | 6
2014-05-07 | 1.9 | 7.5 | 8.7 | 8 | 3 | N/S | 8 | 6 | 1359 | 326 | 3 | 0.2 | 24.29 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-08 | 1.92 | 7.4 | 8.2 | 7 | 3 | N/S | 5 | 4 | 1444 | 386 | 3 | 0.2 | 24.46 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-09 | 3.24 | 7.2 | 8.6 | N/S | N/S | N/S | 10 | 6 | 1145 | 346 | 3 | 0.2 | 15.85 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-10 | 3.36 | 7.2 | 9.2 | N/S | N/S | N/S | 7 | 5 | 1132 | 320 | 1 | 0.1 | 13.18 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-11 | 3.25 | 7.2 | 7.5 | 6 | 4 | N/S | 6 | <4 | 1204 | 332 | 2 | 0.2 | 14.28 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-12 | 3.75 | 7.2 | 7 | 14 | 6 | <5 | 20 | 16 | 992 | 168 | 3 | 0.1 | 12.63 | 1.6 | 0.006 | 5 | 0.6 | 7000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-13 | 4 | 7.1 | 9.9 | 7 | 3 | N/S | 5 | <4 | 1047 | 160 | 2 | 0.1 | 12.86 | 1.3 | N/S | N/S | N/S | N/S | 0.05 | 0.037 | <0.001 | <0.005 | 0.005 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.035 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 84 | 33 | 346 | <8.0 | 5
2014-05-14 | 3.38 | 7.1 | 9.3 | 8 | 3 | N/S | 11 | 9 | 1137 | 196 | 2 | 0.1 | 13.3 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-15 | 3.74 | 7.2 | 8.5 | 3 | 3 | N/S | 6 | 4 | 1043 | 182 | 2 | 0.1 | 12.75 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-16 | 3.83 | 7.2 | 9.9 | N/S | N/S | N/S | <4 | <4 | 1071 | 186 | 1 | 0.1 | 12.77 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-17 | 3.61 | 7.5 | 11.5 | N/S | N/S | N/S | 4 | 4 | 1175 | 238 | 2 | <0.1 | 13.35 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-18 | 3.05 | 7.4 | 11.2 | 5 | 3 | N/S | 5 | 4 | 1256 | 246 | 2 | 0.1 | 13.82 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-19 | 2.64 | 7.5 | 9.9 | 4 | 3 | <5 | 8 | 6 | 1324 | 252 | 2 | 0.2 | 14.94 | 1.8 | 0.005 | <5 | 0.8 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-20 | 2.47 | 7.5 | 10.9 | 5 | 3 | N/S | 6 | 4 | 1341 | 268 | 2 | 0.2 | 16.81 | 1.8 | N/S | N/S | N/S | N/S | 0.07 | 0.044 | <0.001 | <0.005 | <0.005 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | 0.044 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 111 | 40 | 441 | <8.0 | 4
2014-05-21 | 4.06 | 7.5 | 9.8 | 15 | 6 | N/S | 14 | 14 | 1051 | 224 | 2 | 0.2 | 11.41 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-22 | 3.51 | 7.4 | 7.8 | 7 | 4 | N/S | 9 | 6 | 1182 | 244 | 2 | 0.1 | 11.74 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-23 | 3.27 | 7.5 | 7.8 | N/S | N/S | N/S | 15 | 8 | 1422 | 404 | 2 | 0.2 | 14.2 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-24 | 2.38 | 7.5 | 9.2 | N/S | N/S | N/S | 6 | 4 | 1430 | 424 | 2 | 0.4 | 15.4 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-25 | 2.38 | 7.5 | 8.3 | 6 | 3 | N/S | 4 | 4 | 1477 | 428 | 2 | 0.4 | 16.09 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-26 | 2.01 | 7.5 | 9.7 | 6 | 3 | <5 | 5 | 4 | 1210 | 206 | 2 | 0.3 | 18.69 | 2.3 | 0.006 | <5 | 0.9 | 30000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-27 | 2.47 | 7.4 | 7.6 | 6 | 3 | N/S | 5 | 5 | 1183 | 242 | 2 | 0.3 | 19.11 | 2.2 | N/S | N/S | N/S | N/S | 0.06 | 0.038 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.041 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 86 | 33 | 354 | <0.5 | 5
2014-05-28 | 2.5 | 7.4 | 7.7 | 7 | 4 | N/S | <4 | <4 | 1278 | 264 | 3 | 0.3 | 18.25 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-29 | 2.44 | 7.4 | 9.3 | 7 | 3 | N/S | <4 | <4 | 1226 | 286 | 4 | 0.3 | 18.58 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-30 | 2.76 | 7.3 | 7.6 | N/S | N/S | N/S | 5 | <4 | 1273 | 300 | 3 | 0.5 | 17.54 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-05-31 | 2.11 | 7.3 | 7.3 | N/S | N/S | N/S | <4 | <4 | 1426 | 356 | 3 | 0.3 | 18.45 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-01 | 1.88 | 7.5 | 7.8 | 5 | 3 | N/S | 4 | <4 | 1479 | 370 | 3 | 0.3 | 19.97 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-02 | 2.35 | 7.5 | 8.8 | 5 | 3 | <5 | 4 | <4 | 1383 | 262 | 2 | 0.2 | 19.19 | 2.7 | <0.005 | <5 | 0.9 | 8100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-03 | 2 | 7.5 | 7.6 | 4 | <2 | N/S | <4 | <4 | 1272 | 242 | 3 | 0.2 | 20.29 | 2.5 | N/S | N/S | N/S | N/S | 0.05 | 0.039 | <0.001 | <0.005 | 0.005 | <0.1 | <0.1 | <0.02 | 0.006 | <0.2 | <0.005 | 0.036 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 99 | 37 | 397 | 1.9 | 5
2014-06-04 | 2.18 | 7.5 | 8.3 | 5 | 3 | N/S | <4 | <4 | 1196 | 166 | 3 | 0.2 | 21.33 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-05 | 2.03 | 7.6 | 6.9 | 7 | 3 | N/S | 4 | <4 | 1188 | 192 | 2 | 0.3 | 20.58 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-06 | 1.92 | 7.5 | 7.9 | N/S | N/S | N/S | 4 | <4 | 1304 | 296 | 2 | 0.2 | 22.31 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-07 | 1.95 | 7.5 | 7.3 | N/S | N/S | N/S | 4 | <4 | 1377 | 324 | 2 | 0.2 | 21.87 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-08 | 2.52 | 7.5 | 6.7 | 7 | 3 | N/S | 6 | 5 | 1357 | 324 | 2 | 0.2 | 19.17 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-09 | 2.12 | 7.5 | 6.9 | 8 | 5 | <5 | <4 | <4 | 1385 | 358 | 3 | 0.2 | 19.06 | 2.4 | <0.005 | <5 | 0.9 | 3300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-10 | 2.22 | 7.6 | 6.7 | T/X | T/X | N/S | 5 | 4 | 1211 | 266 | 3 | 0.1 | 18.85 | 2.3 | N/S | N/S | N/S | N/S | 0.05 | 0.04 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.028 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 93 | 33 | 366 | T/X | 6
2014-06-11 | 3.89 | 7.4 | 6.6 | 15 | 7 | N/S | 11 | 10 | 788 | 164 | 4 | 0.5 | 7.82 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-12 | 4.28 | 7.2 | 4.5 | T/X | T/X | N/S | 25 | 20 | 874 | 170 | 3 | <0.1 | 8.16 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-13 | 3.45 | 7.4 | 8.7 | N/S | N/S | N/S | 12 | 9 | 1069 | 238 | 2 | 0.1 | 12 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-14 | 2.31 | 7.4 | 6.6 | N/S | N/S | N/S | 6 | 6 | 1309 | 330 | 2 | 0.1 | 16.08 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-15 | 2.08 | 7.5 | 7.4 | 9 | 5 | N/S | 8 | 6 | 1316 | 296 | 2 | 0.2 | 19.68 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-16 | 2.2 | 7.4 | 7.6 | 9 | 4 | <5 | 7 | 5 | 1311 | 278 | 2 | 0.2 | 22.07 | 2.7 | <0.005 | 5 | 0.9 | 4200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-17 | 2.05 | 7.5 | 7.1 | 9 | 6 | N/S | 6 | <4 | 1313 | 264 | 3 | 0.2 | 23.61 | 2.9 | N/S | N/S | N/S | N/S | 0.06 | 0.04 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.031 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 98 | 35 | 390 | 109.6 | 6
2014-06-18 | 2.23 | 7.5 | 7 | 12 | 6 | N/S | 10 | 8 | 1315 | 300 | 3 | 0.2 | 21.82 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-19 | 2.55 | 7.5 | 7.1 | 13 | 6 | N/S | 8 | 7 | 1209 | 280 | 3 | 0.2 | 17.54 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-20 | 2.85 | 7.4 | 7.3 | N/S | N/S | N/S | 19 | 14 | 920 | 190 | 2 | 0.1 | 13.44 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-21 | 2.94 | 7.4 | 6.8 | N/S | N/S | N/S | 27 | 20 | 1019 | 220 | 4 | 0.1 | 13.92 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-22 | 3.48 | 7.5 | 7.4 | 17 | 7 | N/S | 20 | 16 | 938 | 192 | 3 | 0.1 | 11.04 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-23 | 3.3 | 7.4 | 6.1 | 16 | 8 | <5 | 25 | 22 | 996 | 196 | 4 | 0.1 | 12.05 | 1.9 | <0.005 | <5 | 0.7 | 42000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-24 | 3.29 | 7.4 | 7.2 | 14 | 5 | N/S | 14 | 12 | 1046 | 194 | 2 | 0.1 | 13.05 | 1.9 | N/S | N/S | N/S | N/S | 0.06 | 0.038 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.021 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 86 | 33 | 350 | 0.9 | 6
2014-06-25 | 2.3 | 7.7 | 7 | 9 | 4 | N/S | 8 | 7 | 1141 | 226 | 2 | 0.2 | 17.13 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-26 | 2.22 | 7.5 | 6.2 | T/X | T/X | N/S | 4 | <4 | 1153 | 210 | 1 | 0.3 | 20.11 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-27 | 2.21 | 7.4 | 7.4 | N/S | N/S | N/S | 8 | 8 | 1283 | 290 | 1 | 0.2 | 21.03 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-28 | 2.1 | 7.4 | 6.9 | N/S | N/S | N/S | 11 | 9 | 1355 | 308 | 2 | 0.3 | 19.23 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-29 | 2.03 | 7.4 | 6.5 | 8 | 5 | N/S | 10 | 8 | 1354 | 298 | 2 | 0.2 | 19.44 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-06-30 | 2.61 | 7.3 | 5.5 | 9 | 4 | <5 | 10 | 6 | 1077 | 180 | 2 | 0.2 | 14.18 | 2.9 | <0.005 | <5 | 0.8 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-01 | 4.27 | 7.2 | 5.8 | T/X | T/X | N/S | 9 | 6 | 704 | 116 | 1 | 0.2 | 8.11 | 1.3 | N/S | N/S | N/S | N/S | <0.05 | 0.029 | 0.001 | <0.005 | 0.008 | 0.1 | <0.1 | <0.02 | 0.009 | <0.2 | <0.005 | <0.005 | 0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 62 | 24 | 254 | 0.8 | 6
2014-07-02 | 4.28 | 7.2 | 7.3 | 6 | 4 | N/S | 7 | 6 | 1158 | 232 | 2 | 0.2 | 9.2 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-03 | 4.29 | 7.2 | 7.7 | 6 | 5 | N/S | 6 | 4 | 1122 | 172 | 2 | 0.1 | 10.81 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-04 | 3.8 | 7.3 | 6.7 | N/S | N/S | N/S | 8 | 6 | 938 | 122 | 2 | 0.1 | 13.3 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-05 | 2.55 | 7.4 | 6.9 | N/S | N/S | N/S | 6 | 5 | 948 | 134 | 2 | 0.2 | 15.22 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-06 | 2.1 | 7.5 | 5.7 | T/X | T/X | N/S | 5 | 5 | 1033 | 194 | 2 | 0.3 | 17.45 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-07 | 2.36 | 7.5 | 7.4 | T/X | T/X | <5 | 7 | 5 | 982 | 184 | 2 | 0.2 | 16.11 | 2.2 | <0.005 | 10 | 0.8 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-08 | 3.37 | 7.5 | 7 | 7 | 3 | N/S | 6 | 6 | 838 | 130 | 2 | 0.2 | 14.5 | 1.9 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | 0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.007 | <0.2 | <0.005 | <0.005 | 0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 73 | 28 | 296 | 0.8 | 5
2014-07-09 | 2.57 | 7.5 | 5.5 | 7 | 3 | N/S | 5 | 4 | 824 | 142 | 2 | 0.2 | 12.56 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-10 | 2.56 | 7.4 | 7.7 | 3 | <2 | N/S | 6 | 4 | 1051 | 222 | 2 | 0.3 | 17.09 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-11 | 2.24 | 7.5 | 7.3 | N/S | N/S | N/S | 4 | <4 | 1126 | 230 | 2 | 0.2 | 18.81 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-12 | 3.55 | 7.5 | 6.4 | N/S | N/S | N/S | <4 | <4 | 1009 | 226 | 2 | 0.1 | 15.28 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-13 | 4.47 | 7.3 | 6.7 | 3 | 2 | N/S | 6 | 4 | 632 | 124 | 1 | 0.1 | 8.15 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-14 | 4.41 | 7.4 | 5 | 2 | <2 | <5 | 5 | <4 | 816 | 152 | 2 | 0.1 | 9.84 | 1.2 | <0.005 | <5 | 0.6 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-15 | 3.72 | 7.4 | 5.8 | T/X | T/X | N/S | <4 | <4 | 932 | 166 | 1 | 0.2 | 12.22 | 1.5 | N/S | N/S | N/S | N/S | <0.05 | 0.043 | 0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.005 | 0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 91 | 34 | 365 | 6.4 | 5
2014-07-16 | 3 | 7.5 | 9 | 6 | 2 | N/S | <4 | <4 | 1049 | 180 | 2 | 0.2 | 16.13 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-17 | 2.91 | 7.4 | 5.1 | 4 | <2 | N/S | <4 | <4 | 1208 | 254 | 2 | 0.3 | 16.49 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-18 | 2.18 | 7.3 | 9.3 | N/S | N/S | N/S | <4 | <4 | 1243 | 224 | 2 | 0.3 | 16.59 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-19 | 2.05 | 7.4 | 7.7 | N/S | N/S | N/S | 4 | 4 | 1453 | 248 | 2 | 0.3 | 18.52 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-20 | 2.09 | 7.4 | 7.1 | 4 | <2 | N/S | <4 | <4 | 1482 | 276 | 2 | 0.3 | 20.1 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-21 | 2.21 | 7.4 | 7.2 | 3 | <2 | <5 | <4 | <4 | 1476 | 324 | 1 | 0.3 | 21.57 | 3 | <0.005 | <5 | 1 | 3400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-22 | 2.03 | 7.3 | 6.7 | 5 | <2 | N/S | <4 | <4 | 1706 | 374 | 2 | 0.2 | 22.06 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | 0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 94 | 33 | 371 | <0.5 | 4
2014-07-23 | 1.98 | 7.4 | 6 | 5 | 3 | N/S | <4 | <4 | 1512 | 252 | 2 | 0.2 | 22.08 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-24 | 1.81 | 7.2 | 7.5 | 4 | 2 | N/S | 4 | <4 | 1758 | 342 | 2 | 0.3 | 23.73 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-25 | 1.75 | 7.3 | 7.3 | N/S | N/S | N/S | <4 | <4 | 1714 | 460 | 2 | 0.3 | 22.7 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-26 | 1.82 | 7.3 | 7.5 | N/S | N/S | N/S | <4 | <4 | 1805 | 470 | 2 | 0.2 | 21.19 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-27 | 1.77 | 7.4 | 7.3 | 7 | 3 | N/S | <4 | <4 | 1776 | 464 | 2 | 0.3 | 19.8 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-28 | 1.88 | 7.3 | 5.7 | 4 | 3 | <5 | 5 | <4 | 1602 | 310 | 2 | 0.2 | 20.12 | 3.1 | 0.008 | <5 | 1.1 | 23000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-29 | 1.86 | 7.4 | 6.2 | 5 | 3 | N/S | 4 | 4 | 1881 | 424 | 2 | 0.3 | 21.76 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.049 | 0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | 0.002 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 124 | 43 | 485 | <0.5 | 5
2014-07-30 | 1.87 | 7.4 | 6.4 | 4 | 2 | N/S | <4 | <4 | 1856 | 408 | 2 | 0.4 | 22.57 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-07-31 | 1.83 | 7.5 | 7.3 | 3 | <2 | N/S | 6 | 4 | 1768 | 366 | 2 | 0.3 | 23.62 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-01 | 1.82 | 7.4 | 7 | N/S | N/S | N/S | <4 | <4 | 1604 | 334 | 2 | 0.3 | 22.08 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-02 | 1.87 | 7.5 | 6 | N/S | N/S | N/S | <4 | <4 | 1408 | 286 | 5 | 0.3 | 21.64 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-03 | 1.97 | 7.3 | 6 | 4 | 2 | N/S | <4 | <4 | 1416 | 306 | 3 | 0.2 | 20.27 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-04 | 1.85 | 7.5 | 6 | 5 | 3 | <5 | <4 | <4 | 1432 | 324 | 2 | 0.2 | 21.09 | 3.5 | <0.005 | <5 | 1.1 | 57000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-05 | 2.84 | 7.4 | 7 | 3 | 2 | N/S | <4 | <4 | 998 | 132 | 2 | 0.1 | 15.26 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | 0.001 | <0.005 | 0.005 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.006 | 0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 79 | 28 | 313 | 0.6 | 5
2014-08-06 | 2.76 | 7.3 | 7.4 | 4 | 2 | N/S | 6 | 4 | 1066 | 262 | 1 | 0.2 | 16.06 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-07 | 2.31 | 7.3 | 6.5 | 5 | 3 | N/S | 4 | 4 | 1266 | 324 | 6 | 0.3 | 18.74 | 10.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-08 | 1.84 | 7.4 | 5.4 | N/S | N/S | N/S | <4 | <4 | 1295 | 280 | 3 | 0.3 | 22.05 | 5.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-09 | 1.9 | 7.3 | 7.7 | N/S | N/S | N/S | 6 | 4 | 1582 | 370 | 2 | 0.5 | 21.87 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-10 | 1.93 | 7.6 | 7.1 | 8 | 5 | N/S | 8 | 6 | 1884 | 450 | 2 | 0.6 | 21.81 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-11 | 2.68 | 7.4 | 7.2 | 6 | 4 | <5 | 5 | 4 | 1412 | 310 | 2 | 0.3 | 18.28 | 2.7 | <0.005 | <5 | 0.8 | 100000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-12 | 2.76 | 7.4 | 7.5 | 7 | 4 | N/S | 7 | 6 | 1088 | 164 | 3 | 0.2 | 15.35 | 2.3 | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.005 | 0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 88 | 32 | 351 | 7.2 | 5
2014-08-13 | 2.45 | 7.3 | 7.8 | 6 | 3 | N/S | <4 | <4 | 1285 | 242 | 2 | 0.4 | 17.3 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-14 | 1.79 | 7.5 | 8.1 | 6 | 3 | N/S | <4 | <4 | 1598 | 416 | 2 | 0.3 | 21.88 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-15 | 1.78 | 7.4 | 6 | N/S | N/S | N/S | 5 | 4 | 1714 | 410 | 1 | 0.4 | 22.83 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-16 | 1.72 | 7.3 | 7.1 | N/S | N/S | N/S | 4 | <4 | 1626 | 378 | 2 | 0.6 | 22.5 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-17 | 1.75 | 7.3 | 7 | 6 | 3 | N/S | 4 | 4 | 1508 | 330 | 4 | 0.7 | 22.27 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-18 | 1.86 | 7.3 | 7.3 | 6 | 3 | <5 | 6 | 4 | 1378 | 310 | 4 | 1.2 | 23.05 | 3.3 | <0.005 | <5 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-19 | 1.67 | 7.3 | 6 | 5 | 3 | N/S | 5 | 4 | 1268 | 248 | 3 | 0.6 | 23.06 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.017 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 32 | 382 | <0.5 | 6
2014-08-20 | 1.81 | 7.2 | 8.1 | 8 | 3 | N/S | 8 | 8 | 1248 | 240 | 3 | 0.7 | 24.05 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-21 | 2.99 | 7.4 | 7 | 7 | 4 | N/S | 6 | 5 | 940 | 160 | 3 | 0.3 | 18.13 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-22 | 4.14 | 7.2 | 7.2 | N/S | N/S | N/S | 14 | 10 | 836 | 190 | 3 | 0.1 | 10.14 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-23 | 4.3 | 7.2 | 7 | N/S | N/S | N/S | 13 | 9 | 766 | 138 | 2 | 0.2 | 10.48 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-24 | 3.48 | 7.2 | 6.9 | 5 | 3 | N/S | 11 | 8 | 828 | 166 | 1 | 0.2 | 11.94 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-25 | 3.15 | 7.4 | 7.8 | 6 | 3 | <5 | 9 | 8 | 992 | 212 | 1 | 0.2 | 14.08 | 2.1 | 0.005 | <5 | 0.7 | 250000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-26 | 2.96 | 7.4 | 7 | 7 | 3 | N/S | 10 | 6 | 920 | 174 | 1 | 0.2 | 15.31 | 2.2 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.008 | 0.2 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | <0.005 | 0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 80 | 30 | 322 | 1.2 | 6
2014-08-27 | 2.69 | 7.4 | 8.5 | 26 | 23 | N/S | 9 | 5 | 964 | 226 | 2 | 0.1 | 15.88 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-28 | 2.18 | 7.5 | 8.5 | N/A | N/A | N/S | 7 | 4 | 1078 | 258 | 1 | 0.4 | 18.67 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-29 | 2.03 | 7.4 | 8 | N/S | N/S | N/S | 8 | 5 | 1029 | 148 | 2 | <0.1 | 20.3 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-30 | 1.83 | 7.4 | 8.2 | N/S | N/S | N/S | 4 | 4 | 1040 | 154 | 2 | 0.1 | 19.03 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-08-31 | 2.05 | 7.4 | 6.8 | 5 | 3 | N/S | 4 | 4 | 1045 | 156 | 2 | 0.3 | 19.17 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-01 | 2 | 7.3 | 6.5 | 6 | 4 | <5 | <4 | <4 | 1054 | 166 | 2 | 0.3 | 20.69 | 3 | <0.005 | <5 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-02 | 1.96 | 7.3 | 7.8 | 6 | 4 | N/S | <4 | <4 | 1038 | 156 | 2 | 0.3 | 19.49 | 2.8 | N/S | N/S | N/S | 20000 | <0.05 | 0.038 | <0.001 | <0.005 | 0.006 | 0.1 | <0.1 | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 96 | 32 | 374 | 0.5 | 6
2014-09-03 | 1.85 | 7.3 | 7.9 | 5 | 3 | N/S | <4 | <4 | 1120 | 190 | 2 | 0.3 | 20.83 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-04 | 2.03 | 7.4 | 8.6 | 5 | 3 | N/S | <4 | <4 | 1046 | 162 | 2 | 0.2 | 21.11 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-05 | 2.49 | 7.4 | 8.5 | N/S | N/S | N/S | <4 | <4 | 876 | 110 | 1 | 0.2 | 18.72 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-06 | 2.73 | 7.3 | 7.5 | N/S | N/S | N/S | 4 | <4 | 752 | 144 | 1 | 0.2 | 16.85 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-07 | 2.73 | 7.4 | 8.4 | 5 | 3 | N/S | <4 | <4 | 766 | 100 | 1 | 0.2 | 18.66 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-08 | 2.77 | 7.3 | 6.1 | 5 | 3 | <5 | 4 | 4 | 828 | 112 | 2 | 0.2 | 19.45 | 2.5 | <0.005 | <5 | 0.9 | 9900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-09 | 1.96 | 7.4 | 8.4 | 4 | 2 | N/S | <4 | <4 | 1041 | 162 | 1 | 0.4 | 20.36 | 2.6 | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 35 | 393 | <0.5 | 5
2014-09-10 | 3.69 | 7.4 | 8.3 | 6 | 3 | N/S | 8 | 5 | 834 | 142 | 2 | 0.1 | 14.06 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-11 | 4.49 | 7.3 | 9.4 | 5 | 3 | N/S | 6 | 6 | 708 | 124 | 1 | 0.1 | 8.14 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-12 | 3.68 | 7.2 | 9.5 | N/S | N/S | N/S | 4 | 4 | 860 | 116 | 2 | 0.1 | 11.39 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-13 | 3.09 | 7.4 | 9.9 | N/S | N/S | N/S | 4 | <4 | 1028 | 150 | 2 | 0.1 | 15.35 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-14 | 3.03 | 7.4 | 9 | 5 | 3 | N/S | 4 | <4 | 1116 | 154 | 2 | 0.2 | 17.12 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-15 | 2.2 | 7.3 | 9.3 | 5 | 3 | <5 | 4 | 4 | 1167 | 172 | 2 | 0.2 | 19.51 | 2.3 | <0.005 | <5 | 0.8 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-16 | 2.06 | 7.4 | 7.2 | 5 | 2 | N/S | 5 | <4 | 632 | 104 | 2 | 0.2 | 20.72 | 2.5 | N/S | N/S | N/S | N/S | <0.05 | 0.042 | 0.001 | 0.007 | 0.005 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | 0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 34 | 391 | N/S | 5
2014-09-17 | 1.95 | 7.4 | 7.1 | 5 | 2 | N/S | 5 | <4 | 1178 | 162 | 2 | 0.4 | 20.8 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 1.2 | N/S
2014-09-18 | 1.87 | 7.4 | 8.1 | 6 | 3 | N/S | 4 | <4 | 1192 | 178 | 2 | 0.2 | 20.7 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-19 | 1.81 | 7.4 | 8.3 | N/S | N/S | N/S | 5 | 4 | 1182 | 168 | 2 | 0.2 | 21.61 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-20 | 1.88 | 7.4 | 9 | N/S | N/S | N/S | 6 | 6 | 1204 | 166 | 2 | 0.3 | 19.85 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-21 | 2.18 | 7.4 | 8.4 | 5 | 3 | N/S | 6 | 6 | 1238 | 180 | 2 | 0.2 | 20.74 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-22 | 1.76 | 7.5 | 10 | 7 | 3 | <5 | 4 | <4 | 1267 | 228 | 2 | 0.2 | 20.94 | 3.3 | <0.005 | <5 | 1 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-23 | 1.62 | 7.5 | 7.9 | 6 | 3 | N/S | 5 | 4 | 1326 | 204 | 2 | 0.3 | 22.72 | 3.5 | N/S | N/S | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 101 | 33 | 391 | 2.1 | 6
2014-09-24 | 1.68 | 7.3 | 9.7 | 7 | 3 | N/S | 7 | 6 | 1315 | 192 | 2 | 0.3 | 23.28 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-25 | 1.63 | 7.4 | 8.3 | 7 | 4 | N/S | 9 | 8 | 1375 | 250 | 2 | 0.3 | 25.45 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-26 | 1.66 | 7.4 | 8.9 | N/S | N/S | N/S | 12 | 10 | 1349 | 226 | 2 | 0.4 | 21.63 | 3.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-27 | 1.68 | 7.3 | 8.7 | N/S | N/S | N/S | 14 | 11 | 1246 | 248 | 3 | 0.2 | 24.5 | 4.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-28 | 1.75 | 7.3 | 7.4 | 13 | 7 | N/S | 12 | 12 | 1204 | 220 | 3 | 0.6 | 23.52 | 4.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-29 | 1.78 | 7.4 | 8.8 | 14 | 5 | <5 | 20 | 16 | 1218 | 234 | 4 | 0.4 | 25.77 | 4.5 | <0.005 | 6 | 1.1 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-09-30 | 1.66 | 7.5 | 8.5 | 15 | 6 | N/S | 24 | 18 | 1219 | 234 | 3 | 0.2 | 26.54 | 4.1 | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.026 | 0.3 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.006 | 0.002 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 93 | 31 | 360 | 8.7 | 9
2014-10-01 | 1.64 | 7.6 | 8.2 | 18 | 8 | N/S | 29 | 25 | 1096 | 210 | 4 | 0.2 | 25.98 | 4.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-02 | 1.56 | 7.5 | 7.9 | T/X | T/X | N/S | 30 | 24 | 980 | 162 | 5 | 0.1 | 28.55 | 4.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-03 | 3.79 | 7.2 | 8.2 | N/S | N/S | N/S | 33 | 23 | 620 | 124 | 3 | <0.1 | 12.35 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-04 | 4.06 | 7.3 | 8.8 | N/S | N/S | N/S | 24 | 15 | 638 | 106 | <1 | 0.2 | 8.53 | 0.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-05 | 4.01 | 7.4 | 9.2 | 17 | 7 | N/S | 20 | 15 | 738 | 126 | 4 | 1.1 | 9.49 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-06 | 3.53 | 7.4 | 8.1 | 24 | 7 | <5 | 29 | 22 | 806 | 166 | 5 | 1.5 | 11.91 | 1.6 | <0.005 | 8 | 0.7 | 43000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-07 | 2.59 | 7.4 | 7.5 | 13 | 5 | N/S | 18 | 14 | 972 | 168 | 4 | 0.7 | 15.92 | 1.9 | N/S | N/S | N/S | N/S | <0.05 | 0.044 | <0.001 | <0.005 | 0.016 | 0.3 | 0.1 | <0.02 | 0.061 | <0.2 | <0.005 | <0.005 | 0.002 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 91 | 32 | 360 | 3.5 | 7
2014-10-08 | 2.16 | 7.5 | 8 | 9 | 5 | N/S | 9 | 8 | 1002 | 126 | 2 | 0.2 | 19.99 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-09 | 2.02 | 7.4 | 9 | 9 | 3 | N/S | 10 | 8 | 1033 | 186 | 2 | 0.2 | 21.4 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-10 | 2 | 7.4 | 7.5 | N/S | N/S | N/S | 11 | 9 | 988 | 112 | 2 | 0.1 | 21.62 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-11 | 1.96 | 7.4 | 9.5 | N/S | N/S | N/S | 13 | 9 | 954 | 128 | 4 | 0.1 | 22.22 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-12 | 1.94 | 7.4 | 9.9 | 10 | 5 | N/S | 13 | 10 | 1002 | 174 | 4 | 0.1 | 22.67 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-13 | 1.94 | 7.4 | 7.9 | 9 | 4 | <5 | 15 | 12 | 986 | 226 | 2 | <0.1 | 21.4 | 3 | <0.005 | 5 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-14 | 2.83 | 7.3 | 8.2 | 9 | 4 | N/S | 13 | 11 | 810 | 128 | 2 | <0.1 | 16.59 | 2.4 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.014 | 0.2 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | 0.001 | 0.03 | <0.05 | T/X | <0.1 | <6 | 68 | 24 | 269 | T/X | 6
2014-10-15 | 4.22 | 7.1 | 9.2 | 9 | 5 | N/S | 12 | 9 | 642 | 96 | 1 | <0.1 | 11.34 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-16 | 4.29 | 7.2 | 8.7 | 9 | 4 | N/S | 16 | 12 | 700 | 202 | 3 | 0.1 | 10.98 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-17 | 3.17 | 7.3 | 8 | N/S | N/S | N/S | 13 | 11 | 754 | 164 | 1 | <0.1 | 12.74 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-18 | 2.93 | 7.4 | 8.9 | N/S | N/S | N/S | 10 | 8 | 868 | 146 | 1 | <0.1 | 16.39 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-19 | 2.37 | 7.4 | 9.8 | 10 | 4 | N/S | 10 | 8 | 974 | 224 | 2 | 0.2 | 17.82 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-20 | 2.33 | 7.3 | 7.6 | 13 | 6 | <5 | 7 | 6 | 932 | 118 | 3 | 0.1 | 18.45 | 2.5 | 0.006 | 6 | 0.9 | 7100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-21 | 1.94 | 7.3 | 9.7 | 15 | 6 | N/S | 8 | 6 | 976 | 174 | 5 | <0.1 | 18.88 | 5.4 | N/S | N/S | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.009 | 0.2 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | <0.005 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 86 | 31 | 345 | 1.4 | 7
2014-10-22 | 1.9 | 7.3 | 10.1 | 12 | 5 | N/S | 8 | 6 | 964 | 198 | 3 | 0.1 | 21.04 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-23 | 1.91 | 7.3 | 10.1 | 11 | 5 | N/S | 8 | 6 | 1000 | 152 | 5 | 0.1 | 20.1 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-24 | 1.91 | 7.5 | 8.8 | N/S | N/S | N/S | 6 | 4 | 1064 | 200 | 2 | 0.2 | 21.83 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-25 | 2 | 7.5 | 9.8 | N/S | N/S | N/S | 4 | 4 | 1098 | 180 | 2 | 0.2 | 21.72 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-26 | 1.98 | 7.4 | 8.2 | 7 | 3 | N/S | 7 | 6 | 1132 | 178 | 3 | 0.2 | 21.32 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-27 | 1.93 | 7.4 | 8.5 | 8 | 3 | <5 | 6 | 6 | 1130 | 152 | 3 | 0.3 | 20.54 | 2.9 | <0.005 | <5 | 1.1 | 5200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-28 | 1.98 | 7.5 | 8.3 | 9 | 3 | N/S | 6 | 5 | 1023 | 132 | 2 | 0.1 | 20.95 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.008 | 0.2 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | 0.002 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 81 | 29 | 319 | 1.4 | 6
2014-10-29 | 1.84 | 7.5 | 9.2 | 7 | 3 | N/S | 8 | 7 | 980 | 104 | 2 | 0.1 | 22.05 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-30 | 1.86 | 7.5 | 9.9 | 8 | 3 | N/S | 8 | 6 | 982 | 120 | 3 | 0.2 | 21.62 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-10-31 | 1.75 | 7.5 | 9.8 | N/S | N/S | N/S | 7 | 6 | 966 | 160 | 2 | 0.1 | 23.27 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-01 | 1.87 | 7.5 | 9.8 | N/S | N/S | N/S | 4 | <4 | 1052 | 198 | 2 | 0.1 | 23.2 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-02 | 1.99 | 7.4 | 9.5 | 15 | 6 | N/S | 6 | 6 | 984 | 176 | 2 | 0.2 | 22.94 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-03 | 1.77 | 7.4 | 9 | 8 | 3 | <5 | 10 | 7 | 1004 | 170 | 3 | 0.1 | 21.62 | 3.4 | 0.006 | <5 | 1.1 | 4100 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X
2014-11-04 | 1.73 | 7.4 | 9 | 10 | 4 | N/S | 11 | 8 | 1030 | 174 | 4 | 0.1 | 24.04 | 3.7 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.014 | 0.1 | <0.1 | <0.02 | 0.011 | <0.2 | <0.005 | <0.005 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 84 | 31 | 339 | 2.2 | 7
2014-11-05 | 1.64 | 7.3 | 9 | 10 | 4 | N/S | 12 | 10 | 1127 | 216 | 3 | <0.1 | 25.29 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-06 | 1.64 | 7.3 | 9.6 | 10 | 4 | N/S | 10 | 9 | 1122 | 152 | 3 | 0.1 | 24.08 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-07 | 1.64 | 7.4 | 9.8 | N/S | N/S | N/S | 10 | 8 | 1042 | 184 | 3 | 0.1 | 24.88 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-08 | 1.71 | 7.4 | 10 | N/S | N/S | N/S | 10 | 7 | 1053 | 178 | 2 | 0.1 | 23.99 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-09 | 1.75 | 7.4 | 9.8 | 10 | 4 | N/S | 10 | 10 | 1100 | 178 | 4 | 0.2 | 22.94 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-10 | 1.59 | 7.3 | 9.4 | 8 | 3 | <5 | 8 | 5 | 1117 | 138 | 3 | 0.1 | 21.9 | 3 | <0.005 | <5 | 1.1 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-11 | 1.8 | 7.4 | 8.6 | 10 | 5 | N/S | 10 | 8 | 1130 | 130 | 3 | 0.2 | 23.52 | 3.4 | N/S | N/S | N/S | N/S | <0.05 | 0.066 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.019 | <0.2 | <0.005 | 0.024 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 96 | 35 | 384 | 3.3 | 6
2014-11-12 | 1.71 | 7.3 | 9.2 | 8 | 4 | N/S | 8 | 7 | 990 | 122 | 2 | <0.1 | 23.82 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-13 | 1.73 | 7.3 | 9.8 | 9 | 4 | N/S | 10 | 7 | 1070 | 106 | 3 | 0.1 | 23.9 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-14 | 1.67 | 7.5 | 10 | S/X | S/X | S/X | 10 | 9 | 1203 | 176 | 3 | 0.1 | 22.85 | 3.2 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | <6 | S/X | S/X | S/X | S/X | S/X
2014-11-15 | 1.77 | 7.3 | 9.3 | N/S | N/S | N/S | 10 | 9 | 1242 | 184 | 3 | 0.1 | 22.19 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-16 | 1.79 | 7.4 | 9.9 | 8 | 4 | N/S | 12 | 10 | 1168 | 122 | 3 | 0.4 | 22.17 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-17 | 1.77 | 7.4 | 10 | 9 | 3 | <5 | 11 | 8 | 1198 | 164 | 3 | 0.2 | 24.38 | 3.3 | <0.005 | <5 | 1.1 | 3100 | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X | S/X
2014-11-18 | 1.62 | 7.4 | 9.5 | T/X | T/X | N/S | 13 | 10 | 1109 | 140 | 2 | 0.1 | 23.94 | 3 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | 0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 91 | 32 | 359 | 1.2 | 6
2014-11-19 | 1.55 | 7.4 | 9.5 | 11 | 5 | N/S | 12 | 11 | 1054 | 144 | 3 | 0.1 | 9.3 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-20 | 1.66 | 7.5 | 10 | 11 | 5 | N/S | 14 | 12 | 1114 | 204 | 3 | 0.1 | 24.67 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-21 | 1.6 | 7.4 | 10 | N/S | N/S | N/S | 14 | 12 | 1096 | 114 | 3 | <0.1 | 26.17 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-22 | 1.76 | 7.4 | 10 | N/S | N/S | N/S | 14 | 11 | 1112 | 120 | 3 | 0.2 | 25.15 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-23 | 1.78 | 7.4 | 10 | 15 | 6 | N/S | 11 | 9 | 1084 | 112 | 3 | 0.3 | 25.29 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-24 | 3.87 | 7.3 | 10 | 17 | 8 | <5 | 18 | 15 | 814 | 104 | 3 | 0.1 | 13.5 | 1.8 | <0.005 | 5 | 0.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-25 | 3.05 | 7.3 | 8.8 | 9 | 4 | N/S | 10 | 7 | 736 | 94 | 2 | 0.1 | 11.46 | 1.2 | N/S | N/S | N/S | 15000 | <0.05 | 0.025 | 0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | 0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 61 | 25 | 255 | 17.8 | 6
2014-11-26 | 2.81 | 7.4 | 9.2 | 11 | 6 | N/S | 10 | 10 | 926 | 106 | 3 | 0.5 | 15.4 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-27 | 2.11 | 7.4 | 9 | 11 | 7 | N/S | 10 | 9 | 970 | 82 | 3 | 0.9 | 17.27 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-28 | 1.78 | 7.4 | 9.3 | N/S | N/S | N/S | 6 | 6 | 1040 | 160 | 3 | 0.8 | 19.44 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-29 | 1.82 | 7.5 | 9.1 | N/S | N/S | N/S | 9 | 8 | 1029 | 154 | 4 | 0.9 | 20.98 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-11-30 | 1.78 | 7.5 | 9.7 | 11 | 6 | N/S | 10 | 8 | 1060 | 110 | 3 | 0.8 | 20.64 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-01 | 1.63 | 7.5 | 9.1 | 10 | 6 | <5 | 10 | 8 | 1065 | 150 | 3 | 0.4 | 21.92 | 2.7 | <0.005 | 8 | 1 | 5400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-02 | 1.66 | 7.4 | 9.3 | 10 | 5 | N/S | 11 | 9 | 964 | 114 | 3 | 0.2 | 23.06 | 3.1 | N/S | N/S | N/S | N/S | <0.05 | 0.031 | 0.001 | <0.005 | 0.013 | 0.1 | <0.1 | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 80 | 31 | 328 | 3.2 | 6
2014-12-03 | 1.62 | 7.3 | 9.4 | 10 | 5 | N/S | 12 | 9 | 1084 | 148 | 2 | 0.2 | 24.88 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-04 | 1.62 | 7.4 | 9.6 | 8 | 5 | N/S | 11 | 9 | 1104 | 170 | 2 | 0.2 | 25.05 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-05 | 1.57 | 7.4 | 9.3 | N/S | N/S | N/S | 12 | 11 | 1080 | 116 | 2 | 0.2 | 23.98 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-06 | 1.61 | 7.4 | 9.7 | N/S | N/S | N/S | 9 | 7 | 1092 | 168 | 2 | 0.2 | 24.22 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-07 | 1.77 | 7.5 | 9.8 | 7 | 4 | N/S | 8 | 7 | 1108 | 146 | 2 | 0.3 | 24.56 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-08 | 2.03 | 7.4 | 10 | 10 | 4 | <5 | 11 | 8 | 1084 | 184 | 3 | 0.7 | 23.7 | 3.1 | <0.005 | 5 | 1 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-09 | 1.78 | 7.4 | 9.5 | 7 | 4 | N/S | 8 | 8 | 1030 | 116 | 2 | 0.3 | 22.14 | 3.2 | N/S | N/S | N/S | N/S | <0.05 | 0.032 | 0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 83 | 32 | 339 | 1 | 6
2014-12-10 | 1.73 | 7.4 | 8.9 | 6 | 4 | N/S | 8 | 7 | 1045 | 142 | 2 | 0.2 | 23.44 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-11 | 1.69 | 7.4 | 9.7 | 7 | 4 | N/S | 10 | 8 | 1114 | 150 | 2 | 0.2 | 23.98 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-12 | 1.71 | 7.4 | 9.7 | N/S | N/S | N/S | 12 | 8 | 1083 | 164 | 2 | 0.1 | 22.9 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-13 | 1.91 | 7.4 | 9.7 | N/S | N/S | N/S | 11 | 9 | 1063 | 130 | 3 | 0.9 | 22.41 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-14 | 1.86 | 7.4 | 8.9 | 8 | 5 | N/S | 10 | 8 | 1060 | 116 | 3 | 1.3 | 21.13 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-15 | 1.91 | 7.4 | 9.7 | 10 | 5 | <5 | 12 | 8 | 1064 | 154 | 3 | 0.9 | 21.93 | 3 | 0.005 | 6 | 1.1 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-16 | 2.09 | 7.4 | 9.8 | 6 | 4 | N/S | 8 | 6 | 1040 | 164 | 2 | 0.3 | 20.78 | 2.8 | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 84 | 32 | 342 | 2.2 | 6
2014-12-17 | 1.99 | 7.4 | 9.8 | 7 | 4 | N/S | 10 | 9 | 1209 | 186 | 2 | 0.3 | 22.18 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-18 | 1.92 | 7.4 | 8.5 | 6 | 5 | N/S | 14 | 11 | 1254 | 172 | 2 | 0.2 | 23.05 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-19 | 1.87 | 7.6 | 8.4 | N/S | N/S | N/S | 11 | 9 | 1187 | 184 | 2 | 0.1 | 22.81 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-20 | 1.98 | 7.5 | 9.4 | N/S | N/S | N/S | 12 | 9 | 1140 | 168 | 3 | 1.1 | 21.07 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-21 | 1.89 | 7.6 | 8.6 | 8 | 6 | N/S | 10 | 8 | 1058 | 128 | 4 | 1.7 | 21.02 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-22 | 2.19 | 7.5 | 8.8 | 10 | 5 | <5 | 11 | 10 | 948 | 128 | 3 | 0.8 | 18.05 | 2.6 | <0.005 | <5 | 0.9 | 7700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-23 | 3 | 7.4 | 8.9 | 8 | 3 | N/S | 14 | 11 | 808 | 94 | 2 | 0.1 | 15.12 | 1.8 | N/S | N/S | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 71 | 28 | 290 | 1 | 6
2014-12-24 | 3 | 7.4 | 10 | 9 | 4 | N/S | 13 | 10 | 840 | 146 | 2 | 0.5 | 14.57 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-25 | 2.95 | 7.5 | 9.1 | 12 | 5 | N/S | 11 | 11 | 844 | 118 | 6 | 3 | 14.66 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-26 | 2.39 | 7.5 | 8.4 | N/S | N/S | N/S | 9 | 7 | 846 | 140 | 6 | 3.2 | 17.49 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-27 | 2.36 | 7.4 | 8.6 | N/S | N/S | N/S | 9 | 7 | 870 | 132 | 5 | 2.1 | 18.59 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-28 | 2.1 | 7.5 | 9.8 | 13 | 6 | N/S | 8 | 8 | 856 | 158 | 5 | 1.8 | 20.35 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-29 | 2.01 | 7.4 | 9.9 | T/X | T/X | <5 | 11 | 10 | 854 | 170 | 4 | 0.9 | 22.72 | 3.2 | <0.005 | <5 | 1 | 7600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2014-12-30 | 2.06 | 7.4 | 9.1 | 14 | 5 | N/S | 15 | 12 | 856 | 110 | 4 | 0.5 | 22.39 | 3.3 | N/S | N/S | N/S | N/S | <0.05 | 0.03 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 78 | 32 | 326 | <10.0 | 7
2014-12-31 | 2.03 | 7.4 | 9.2 | 18 | 6 | N/S | 17 | 14 | 876 | 150 | 4 | 0.7 | 23.09 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
PQL |  |  |  | 2 | 2 | 5 | 4 | 4 | 100 |  | 1 | 0.1 | 0.15 | 0.2 | 0.005 | 5 | 0.1 | 10 | 0.05 | 0.004 | 0.001 | 0.005 | 0.005 | 0.1 | 0.1 | 0.02 | 0.001 | 0.2 | 0.005 | 0.005 | 0.001 | 0.01 | 0.05 | 0.001 | 0.1 | 6 | 1 | 1 |  | 0.5 | 1
Observations | 365 | 361 | 365 | 241 | 241 | 52 | 364 | 364 | 361 | 361 | 364 | 364 | 364 | 364 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 49 | 52
Minimum | 1.54 | 7 | 4.5 | 2 | <2 | <5 | <4 | <4 | 620 | 68 | <1 | <0.1 | 7.82 | 0.2 | <0.005 | <5 | 0.5 | 1300 | <0.05 | 0.025 | <0.001 | <0.005 | <0.005 | <0.1 | <0.1 | <0.02 | 0.006 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 61 | 24 | 254 | <0.5 | 4
Mean | 2.4 | 7.4 | 8.7 | 9 | <5 | <5 | <9 | <8 | 1182 | 198 | <3 | <0.4 | 18.76 | 2.5 | <0.005 | <6 | 0.9 | 19450 | <0.05 | 0.038 | <0.001 | <0.005 | <0.010 | <0.1 | <0.1 | <0.02 | 0.012 | <0.2 | <0.005 | <0.018 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 87.6346 | 32.2308 | 351.5577 | <13.5 | 6
Maximum | 4.59 | 7.7 | 13 | 30 | 23 | 19 | 38 | 30 | 1884 | 470 | 6 | 3.2 | 28.55 | 10.1 | 0.008 | 12 | 1.1 | 250000 | 0.07 | 0.066 | 0.001 | 0.007 | 0.027 | 0.3 | 0.1 | <0.02 | 0.061 | <0.2 | 0.005 | 0.085 | 0.002 | 0.06 | <0.05 | <0.001 | <0.1 | <6 | 124 | 43 | 485 | 312 | 10
Std Dev | 0.79 | 0.1 | 1.4 | 4 | 2 | 2 | 5 | 4 | 238 | 75 | 1 | 0.4 | 4.65 | 0.9 | 0.001 | 2 | 0.2 | 36979 | 0.01 | 0.007 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0.018 | 0 | 0.01 | 0 | 0 | 0 | 0 | 11.5911 | 3.7762 | 43.25 | 46.2 | 1
January 1, 2, 3, 2014 TS, TVS T/X: Insufficient sample volume for analysis. Sample discarded.
January 4, 17, 24, 2014 P-TOT, TKN: Sample MS Recovery failed but LCS passed.
January 18, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
January 23, 26, 27 2014 BOD5, CBOD5, T/X: Batch LCS failure.
February 1, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
February 15, 16, 17, 18, 2014 pH N/S: pH meter broken.
February 27, 2014 S/X: Non representative sample.
March 2, 9, 11, 23, 2014 BOD5, CBOD5, T/X: Batch LCS failure.
March 19, 26, 29, 2014 P-TOT, TKN: Sample MS Recovery failed but LCS passed.
March 24, 2014 F, T/X: Sample never arrived at laboratory.
April 1, 2014 Hg LL T/X: MS failure; Unable to overcome matrix effect. Result not reportable.
April 10, 2014 P-TOT, TKN: Sample MS Recovery failed but LCS passed.
April 20, 24, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
April 29, 2014 BOD5, CBOD5, T/X: Batch LCS failure.
May 23, 31, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
June 9, 2014 F: Air spike on CCV peak, all other criteria passed.
June 10, 2014 Hg LL T/X: MS failure; Unable to overcome matrix effect. Result not reportable.
June 10, 12, 26, 2014 BOD5, CBOD5, T/X: Batch LCS failure.
June 30, 2014 P-TOT, TKN: Sample MS Recovery failed but LCS passed.
July 1, 6, 7, 15, 2014 BOD5, CBOD5, T/X: Batch LCS failure.
July 3, 2014 BOD5, CBOD5: The DO depletion for the dilution water blank exceeded 0.2 mg/L.
July 7, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
July 24, 2014 P-TOT, TKN: Sample MS Recovery failed but LCS passed.
August 21, 30, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
August 28, 2014 BOD5, CBOD5 N/A: Inappropriate dilutions.
September 10, 14, 18, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
October 2, 2014 BOD5, CBOD5, T/X: Batch LCS failure.
October 8, 12, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
October 14, 2014 Be T/X: LCS failure. No reruns necessary-sampling frequency requirements fulfilled.
October 14, 2014 Hg LL T/X: Sampling error; Test not assigned by mistake.
October 16, 2014 TKN: Sample MS Recovery failed but LCS passed.
November 18, 2014 CBOD5, T/X: CBOD5>BOD5.
November 29, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
December 1, 2014 FOG: Aliquot refrigerated but not chemically preserved. Acidified before analysis.
December 10, 2014 NO2+NO3_N: Sample MS Recovery failed but LCS passed.
December 29, 2014 BOD5, CBOD5, T/X: Batch water blank failure.

## Lemont Outfall 2015
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2015-01-01 | 1.96 | 7.4 | 9.8 | 18 | 6 | N/S | 16 | 13 | 1026 | 194 | 4 | 0.7 | 22.66 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-02 | 1.77 | 7.4 | 9.7 | N/S | N/S | N/S | 15 | 15 | 1042 | 188 | 3 | 0.6 | 23.4 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-03 | 2.21 | 7.4 | 10 | N/S | N/S | N/S | 21 | 20 | 1127 | 168 | 4 | 0.4 | 19.49 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-04 | 3.2 | 7.2 | 10 | 18 | 8 | N/S | 20 | 18 | 1125 | 142 | 3 | 0.1 | 14.63 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-05 | 2.87 | 7.2 | 9.4 | 20 | 6 | <5 | 18 | 12 | 1178 | 142 | 3 | 0.4 | 15.5 | 2 | 0.007 | 9 | N/S | 0.7 | 7800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-06 | 2.1 | 7.3 | 8 | 12 | 6 | N/S | 15 | 11 | 1143 | 138 | 2 | 0.2 | 17.61 | 2.2 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.034 | 0.001 | <0.005 | 0.011 | 0.1 | 0.1 | <0.02 | 0.011 | <0.2 | <0.005 | 0.009 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 83 | 34 | 348 | <10.0 | 6
2015-01-07 | 2.11 | 7.4 | 9.6 | 11 | 6 | N/S | 11 | 11 | 1070 | 148 | 3 | 0.2 | 18.85 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-08 | 1.98 | 7.4 | 9.8 | 12 | 5 | N/S | 13 | 8 | 1041 | 144 | 3 | 0.1 | 22.45 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-01-09 | 1.89 | 7.3 | 9.7 | N/S | N/S | N/S | 10 | 10 | 1096 | 182 | 2 | 0.2 | 21.21 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-10 | 1.84 | 7.3 | 9.5 | N/S | N/S | N/S | 9 | 7 | 1070 | 184 | 3 | 0.4 | 22.76 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-11 | 1.98 | 7.3 | 9.6 | 14 | 6 | N/S | 10 | 8 | 1117 | 180 | 4 | 1.7 | 20.32 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-12 | 1.79 | 7.3 | 9.2 | 16 | 5 | <5 | 11 | 10 | 1294 | 146 | 3 | 1.1 | 21.78 | 3 | 0.005 | 5 | N/S | 1 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-13 | 1.75 | 7.3 | 9.8 | 11 | 4 | N/S | 10 | 9 | 1318 | 144 | 3 | 0.3 | 23.95 | 3 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.038 | 0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.01 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 92 | 35 | 373 | 0.8 | 6
2015-01-14 | 1.96 | 7.3 | 9.8 | 11 | 5 | N/S | 10 | 9 | 1232 | 152 | 3 | 0.3 | 23.69 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-15 | 1.89 | 7.4 | 9.8 | 11 | 5 | N/S | 9 | 8 | 1198 | 152 | 3 | 0.3 | 23.15 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-16 | 1.84 | 7.4 | 9.8 | N/S | N/S | N/S | 11 | 8 | 1250 | 190 | 3 | 0.4 | 23.2 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-17 | 2.03 | 7.5 | 9.1 | N/S | N/S | N/S | 11 | 9 | 1258 | 154 | 3 | 1 | 22.48 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-18 | 2.3 | 7.4 | 10 | 13 | 8 | N/S | 12 | 12 | 1690 | 196 | 2 | 0.9 | 18.39 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-19 | 2.48 | 7.5 | 8.4 | 13 | 6 | <5 | 14 | 12 | 1662 | 220 | 3 | 1 | 16.52 | 2.3 | 0.005 | <5 | N/S | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-20 | 2.27 | 7.4 | 10 | 14 | 7 | N/S | 10 | 10 | 1592 | 200 | 3 | 0.8 | 17.88 | 2.5 | N/S | N/S | N/S | N/S | 3700 | <0.05 | 0.046 | 0.002 | <0.005 | 0.013 | 0.1 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.006 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 100 | 40 | 416 | <0.5 | 6
2015-01-21 | 2.04 | 7.4 | 9.5 | 12 | 6 | N/S | 12 | 9 | 1564 | 214 | 2 | 0.5 | 19.81 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-22 | 2.16 | 7.3 | 9.8 | 12 | 7 | N/S | 14 | 12 | 1472 | 158 | 2 | 0.3 | 20.15 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-23 | 2.05 | 7.4 | 9.8 | N/S | N/S | N/S | 15 | 12 | 1448 | 202 | 3 | 0.4 | 22.2 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-24 | 2.11 | 7.4 | 9.6 | N/S | N/S | N/S | 23 | 20 | 1368 | 200 | 4 | 1.1 | 21.21 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-25 | 2.08 | 7.4 | 8.3 | 22 | 14 | N/S | 28 | 24 | 1378 | 192 | 5 | 1.8 | 19.36 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-26 | 2.15 | 7.4 | 8.9 | 26 | 17 | 7 | 30 | 26 | 1500 | 180 | 6 | 2.7 | 18.16 | 2.9 | 0.006 | 7 | N/S | 0.9 | 24000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-27 | 1.95 | 7.3 | 9.6 | 19 | 10 | N/S | 20 | 16 | 1502 | 196 | 3 | 0.5 | 17.54 | 2.5 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.044 | <0.001 | <0.005 | 0.019 | 0.2 | N/S | <0.02 | 0.013 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 96 | 38 | 397 | 7.2 | 7
2015-01-28 | 1.96 | 7.4 | 9.1 | 16 | 11 | N/S | 14 | 13 | 1434 | 152 | 3 | 0.4 | 21.11 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-29 | 1.89 | 7.4 | 9.4 | 16 | 9 | N/S | 19 | 17 | 1450 | 182 | 4 | 0.4 | 21.38 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-30 | 1.72 | 7.4 | 9.8 | N/S | N/S | N/S | 16 | 15 | 1312 | 156 | 4 | 1 | 22.44 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-01-31 | 1.8 | 7.6 | 8.4 | N/S | N/S | N/S | 17 | 14 | 1344 | 170 | 4 | 1.5 | 21.78 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-01 | 1.88 | 7.3 | 7.7 | 15 | 8 | N/S | 17 | 16 | 1484 | 182 | 4 | 0.3 | 22.64 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-02 | 0 | 7.3 | 9.8 | 21 | 7 | <5 | 12 | 12 | 1836 | 222 | 3 | 0.9 | 22.12 | 2.8 | 0.008 | 5 | S/X | 0.9 | 6300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-03 | 1.95 | 7.3 | 9.5 | 13 | 6 | N/S | 12 | 10 | 1828 | 166 | 2 | 0.3 | 22.31 | 2.8 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.05 | <0.001 | <0.005 | 0.014 | 0.1 | 0.1 | <0.02 | 0.017 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 102 | 41 | 423 | 1.5 | 6
2015-02-04 | 1.93 | 7.3 | 9.8 | 14 | 7 | N/S | 12 | 10 | 1717 | 148 | 3 | 0.3 | 23.01 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-05 | 1.87 | 7.3 | 9.8 | 16 | 8 | N/S | 15 | 12 | 1732 | 190 | 3 | 0.4 | 24.31 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-06 | 1.86 | 7.4 | 9.8 | N/S | N/S | N/S | 19 | 15 | 1610 | 170 | 3 | 0.3 | 24 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-07 | 2.05 | 7.4 | 9.9 | N/S | N/S | N/S | 22 | 19 | 1537 | 164 | 4 | 0.7 | 22.68 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-08 | 2.68 | 7.3 | 9.5 | 16 | 10 | N/S | 20 | 17 | 1889 | 172 | 2 | 0.3 | 18.78 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-09 | 2.89 | 7.3 | 9.9 | 17 | 8 | <5 | 22 | 21 | 2046 | 208 | 3 | 0.4 | 15.82 | 1.9 | 0.009 | 10 | N/S | 0.6 | 4800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-10 | 2.38 | 7.3 | 9.7 | 18 | 9 | N/S | 23 | 20 | 1853 | 224 | 3 | 0.2 | 16.47 | 2 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.057 | <0.001 | <0.005 | 0.02 | 0.2 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | <0.005 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 110 | 45 | 459 | 4.4 | 5
2015-02-11 | 1.96 | 7.3 | 9.9 | 17 | 11 | N/S | 23 | 20 | 1690 | 188 | 2 | 0.2 | 17.51 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-12 | 2.07 | 7.5 | 9.7 | 15 | 9 | N/S | 16 | 15 | 1612 | 190 | 3 | 0.2 | 18.03 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-13 | 1.94 | 7.4 | 9.9 | N/S | N/S | N/S | 10 | 9 | 1498 | 178 | 2 | 0.2 | 18.2 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-14 | 1.91 | 7.5 | 9.9 | N/S | N/S | N/S | 9 | 8 | 1414 | 166 | 2 | 0.2 | 18.69 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-15 | 1.89 | 7.5 | 9.9 | 9 | 7 | N/S | 10 | 6 | 1294 | 140 | 2 | 0.2 | 19.09 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-16 | 2.11 | 7.4 | 9.5 | 10 | 7 | <5 | 9 | 8 | 1226 | 144 | 3 | 0.7 | 19.56 | 2.4 | 0.006 | 6 | N/S | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-17 | 1.82 | 7.5 | 9.3 | 10 | 5 | N/S | 12 | 10 | 1187 | 148 | 3 | 0.3 | 17.47 | 2.4 | N/S | N/S | N/S | N/S | 2700 | <0.05 | 0.039 | 0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 90 | 37 | 379 | 2.1 | 6
2015-02-18 | 1.77 | 7.4 | 9.9 | 12 | 7 | N/S | 11 | 8 | 1190 | 106 | 3 | 0.4 | 19.56 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-19 | 1.77 | 7.4 | 9.9 | 11 | 8 | N/S | 14 | 11 | 1200 | 148 | 3 | 0.7 | 19.63 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-20 | 1.71 | 7.4 | 9.9 | N/S | N/S | N/S | 11 | 11 | 1193 | 142 | 3 | 1 | 18.43 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-21 | 1.82 | 7.4 | 10 | N/S | N/S | N/S | 13 | 12 | 1202 | 150 | 5 | 2.4 | 16.82 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-22 | 1.82 | 7.4 | 9.9 | 11 | 8 | N/S | 10 | 8 | 1144 | 116 | 6 | 3.8 | 16.43 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-23 | 1.71 | 7.4 | 9.8 | 11 | 6 | <5 | 8 | 6 | 1128 | 116 | 6 | 2.6 | 18.54 | 2.9 | 0.006 | <5 | N/S | 1.1 | 2100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-24 | 1.71 | 7.5 | 10 | 9 | 4 | N/S | 7 | 7 | 1200 | 160 | 3 | 1.2 | 20.38 | 2.9 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.04 | 0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 98 | 37 | 398 | 19.4 | 6
2015-02-25 | 1.68 | 7.5 | 10 | T/X | T/X | N/S | 7 | 6 | 1102 | 114 | 3 | 1 | 21.78 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-26 | 1.67 | 7.4 | 10 | 9 | 4 | N/S | 6 | 5 | 1190 | 120 | 3 | 0.8 | 21.76 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-27 | 1.69 | 7.4 | 9 | N/S | N/S | N/S | 7 | 6 | 1313 | 158 | 2 | 0.7 | 23.62 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-02-28 | 1.79 | 7.5 | 9 | N/S | N/S | N/S | 7 | 7 | 1362 | 168 | 3 | 1.8 | 21.56 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-01 | 1.81 | 7.6 | 9 | T/X | T/X | N/S | 8 | 6 | 1396 | 192 | 5 | 2.5 | 20.97 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-02 | 1.74 | 7.6 | 9 | 10 | 5 | <5 | 6 | 6 | 1432 | 186 | 4 | 2.1 | 21.78 | 3.7 | 0.008 | 8 | N/S | 1.1 | 4800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-03 | 1.79 | 7.4 | 10 | 13 | 7 | N/S | 13 | 9 | 1524 | 134 | 4 | 1.8 | 21.93 | 3.9 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.013 | 0.1 | <0.1 | <0.02 | 0.015 | <0.2 | <0.005 | 0.009 | <0.001 | 0.05 | <0.05 | <0.001 | <0.1 | <6 | 98 | 38 | 401 | 1.5 | 6
2015-03-04 | 1.79 | 7.3 | 10 | 13 | 8 | N/S | 16 | 12 | 1750 | 128 | 4 | 1 | 23.48 | 4.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-05 | 1.55 | 7.4 | 10 | 25 | 16 | N/S | 24 | 20 | 1663 | 140 | 6 | 2.7 | 20.3 | 4.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-06 | 1.71 | 7.4 | 10 | N/S | N/S | N/S | 23 | 19 | 1450 | 170 | 6 | 2.1 | 21.56 | 4.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-07 | 2.05 | 7.4 | 10 | N/S | N/S | N/S | 20 | 18 | 1511 | 206 | 6 | 1.9 | 20.82 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-08 | 2.18 | 7.3 | 10 | 13 | 9 | N/S | 17 | 14 | 1817 | 226 | 4 | 1.7 | 17.36 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-09 | 2.28 | 7.3 | 10 | 11 | 7 | <5 | 13 | 10 | 1942 | 214 | 3 | 0.6 | 15.97 | 2.5 | 0.01 | 5 | N/S | 0.8 | 3500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-03-10 | 3 | 7.4 | 10 | 9 | 4 | N/S | 5 | 4 | 1968 | 188 | 2 | 0.2 | 12.58 | 1.6 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.05 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 95 | 40 | 402 | 2.9 | 4
2015-03-11 | 2.98 | 7.3 | 9.9 | 8 | 5 | N/S | 10 | 8 | 1754 | 196 | 4 | 0.2 | 10.64 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-12 | 3.34 | 7.3 | 9.9 | 8 | 5 | N/S | 11 | 9 | 1624 | 172 | 3 | 0.2 | 10.56 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-13 | 3.2 | 7.3 | 9.8 | N/S | N/S | N/S | 10 | 8 | 1560 | 164 | 4 | 0.2 | 11.61 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-14 | 3.05 | 7.4 | 7.2 | N/S | N/S | N/S | 11 | 9 | 1524 | 192 | 3 | 0.4 | 12.94 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-15 | 3.01 | 7.3 | 8.6 | T/X | T/X | N/S | 8 | 7 | 1472 | 176 | 6 | 1.5 | 13.02 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-16 | 2.63 | 7.4 | 9.9 | 10 | 4 | <5 | 6 | 6 | 1389 | 162 | 4 | 1.5 | 12.99 | 1.9 | 0.012 | 5 | N/S | 0.7 | 2400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-03-17 | 1.95 | 7.3 | 9.5 | 8 | 5 | N/S | 6 | 5 | 1341 | 168 | 3 | 0.2 | 17.06 | 2.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 94 | 41 | 403 | 2.1 | 5
2015-03-18 | 2.24 | 7.5 | 9.9 | 10 | 6 | N/S | 12 | 9 | 1260 | 162 | 3 | 0.3 | 19.64 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-19 | 2.05 | 7.3 | 9.6 | 11 | 6 | N/S | 8 | 7 | 1203 | 170 | 3 | 0.2 | 20.36 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-20 | 2.26 | 7.3 | 9.9 | N/S | N/S | N/S | 13 | 10 | 1142 | 150 | 4 | 0.4 | 19.51 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-21 | 2.02 | 7.3 | 9.9 | N/S | N/S | N/S | 13 | 10 | 1151 | 150 | 3 | 0.6 | 19.6 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-22 | 2.12 | 7.2 | 9.9 | 18 | 8 | N/S | 13 | 12 | 1202 | 156 | 4 | 1.8 | 19.36 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-23 | 1.84 | 7.4 | 10 | 15 | 7 | <5 | 12 | 11 | 1362 | 186 | 5 | 0.8 | 19.95 | 2.8 | 0.007 | <5 | N/S | 0.9 | 4600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 6 | N/S | N/S | N/S | N/S | N/S
2015-03-24 | 2.55 | 7.3 | 9.9 | 14 | 7 | N/S | 12 | 11 | 1650 | 216 | 4 | 0.7 | 18.19 | 3.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.046 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 104 | 42 | 434 | 2.7 | 6
2015-03-25 | 3.02 | 7.2 | 9.7 | 11 | 7 | N/S | 10 | 9 | 1584 | 190 | 3 | 0.3 | 15.05 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-26 | 2.45 | 7.3 | 9.9 | 10 | 7 | N/S | 10 | 8 | 1552 | 186 | 4 | 0.2 | 15.47 | 4.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-27 | 2.49 | 7.3 | 9.9 | N/S | N/S | N/S | 7 | 6 | 1472 | 198 | 3 | 0.4 | 17.3 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-28 | 2.26 | 7.3 | 8.1 | N/S | N/S | N/S | 6 | 6 | 1380 | 186 | 10 | 1 | 17.74 | 12.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-29 | 1.95 | 7.3 | 10 | 10 | 5 | N/S | 6 | 6 | 1328 | 160 | 2 | 0.6 | 18.52 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-03-30 | 2.28 | 7.2 | 7.9 | 11 | 4 | <5 | 6 | 6 | 1350 | 158 | 3 | 0.9 | 18.96 | 1.9 | <0.005 | <5 | N/S | 0.9 | 3300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-03-31 | 1.94 | 7.2 | 7.2 | 9 | 4 | N/S | 8 | 6 | 1344 | 184 | 2 | 0.4 | 19.85 | 2.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 76 | 32 | 319 | 0.9 | 6
2015-04-01 | 1.91 | 7.3 | 9.5 | 9 | 5 | N/S | 6 | 5 | 1212 | 136 | 2 | 0.2 | 20.74 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-02 | 2.79 | 7.4 | 9.9 | 8 | 5 | N/S | 8 | 6 | 1164 | 148 | 2 | 0.1 | 17.45 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-03 | 3.13 | 7.3 | 10 | N/S | N/S | N/S | 6 | 5 | 1261 | 178 | 2 | 0.1 | 13.41 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-04 | 3.23 | 7.3 | 9.8 | N/S | N/S | N/S | 9 | 7 | 1224 | 156 | 3 | 0.9 | 12.96 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-05 | 2.46 | 7.3 | 9.8 | 7 | 5 | N/S | 6 | 5 | 1182 | 138 | 3 | 0.7 | 13.92 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-06 | 2.06 | 7.4 | 10 | T/X | T/X | <5 | 5 | 4 | 1225 | 180 | 2 | 0.2 | 16.73 | 1.9 | <0.005 | <5 | N/S | 0.8 | 9700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-04-07 | 2.31 | 7.4 | 9.8 | 4 | 3 | N/S | <4 | <4 | 1254 | 136 | 4 | 0.1 | 16.95 | 1.8 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.041 | 0.001 | <0.005 | 0.018 | 0.1 | <0.1 | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 98 | 41 | 413 | 0.6 | 5
2015-04-08 | 2.08 | 7.4 | 9.9 | 5 | 4 | N/S | 6 | 4 | 1285 | 188 | 3 | 0.1 | 18.29 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-09 | 3.59 | 7.4 | 10 | T/X | T/X | N/S | 4 | 4 | 990 | 138 | 2 | <0.1 | 12.5 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-10 | 4.35 | 7.3 | 9.9 | N/S | N/S | N/S | 8 | 6 | 880 | 126 | 1 | <0.1 | 8.62 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-11 | 4.2 | 7.3 | 9.8 | N/S | N/S | N/S | 8 | 5 | 1010 | 122 | 3 | <0.1 | 10.39 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-12 | 3.32 | 7.3 | 10 | 6 | 3 | N/S | 8 | 7 | 1082 | 146 | 3 | 0.2 | 12.28 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-13 | 3.19 | 7.3 | 7.8 | 5 | 3 | <5 | 5 | 4 | 1055 | 118 | 2 | 0.1 | 14.91 | 1.4 | 0.005 | <5 | N/S | 0.7 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-04-14 | 3.24 | 7.4 | 8.2 | T/X | T/X | N/S | 6 | 5 | 1212 | 192 | 1 | 0.1 | 15.3 | 1.5 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.039 | 0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 90 | 39 | 383 | 0.5 | 4
2015-04-15 | 2.94 | 7.3 | 9.9 | 6 | 3 | N/S | 4 | 4 | 1243 | 218 | 2 | 0.1 | 16.82 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-16 | 2.51 | 7.4 | 9.9 | 6 | 3 | N/S | 6 | 4 | 1157 | 156 | 1 | 0.1 | 17.53 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-17 | 2.44 | 7.4 | 9.8 | N/S | N/S | N/S | 6 | 4 | 1175 | 136 | 2 | 0.3 | 16.65 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-18 | 2.38 | 7.4 | 9.8 | N/S | N/S | N/S | <4 | <4 | 1169 | 150 | 2 | 0.1 | 16.93 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-19 | 2.3 | 7.4 | 10 | 5 | 2 | N/S | 7 | 5 | 1143 | 174 | 2 | 0.1 | 17.61 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-20 | 3.2 | 7.3 | 9.9 | 6 | 3 | <5 | 7 | 7 | 1030 | 136 | 2 | 0.1 | 14.45 | 1.7 | 0.009 | <5 | N/S | 0.6 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-04-21 | 3.15 | 7.4 | 9.6 | 5 | 4 | N/S | 7 | 5 | 1237 | 196 | 2 | <0.1 | 15.09 | 1.5 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 102 | 41 | 424 | 1.3 | 4
2015-04-22 | 3 | 7.4 | 10 | 6 | 3 | N/S | 4 | 4 | 1339 | 204 | 2 | 0.1 | 17.01 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-23 | 2.45 | 7.4 | 9.9 | 5 | 3 | N/S | <4 | 4 | 1360 | 150 | 2 | 0.1 | 18.28 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-24 | 2.29 | 7.4 | 9.9 | N/S | N/S | N/S | 6 | 4 | 1456 | 192 | 2 | 0.1 | 18.54 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-25 | 3.28 | 7.3 | 8 | N/S | N/S | N/S | 6 | 4 | 1200 | 160 | 2 | <0.1 | 14.37 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-26 | 4.09 | 7.4 | 8.8 | T/X | T/X | N/S | 6 | 5 | 1054 | 118 | 2 | <0.1 | 11.55 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-27 | 3.89 | 7.3 | 9 | 7 | 5 | <5 | 6 | 5 | 1153 | 148 | 2 | 0.1 | 13 | 1.3 | <0.005 | <5 | N/S | 0.7 | 3800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-04-28 | 3.31 | 7.3 | 9.5 | 4 | 7 | N/S | 6 | 5 | 1167 | 138 | 2 | 0.1 | 14.77 | 1.6 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | 0.024 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 94 | 41 | 403 | <0.5 | 5
2015-04-29 | 2.51 | 7.5 | 9.6 | 7 | 3 | N/S | 6 | 5 | 1222 | 188 | 2 | 0.2 | 16.37 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-04-30 | 2.33 | 7.4 | 9.4 | 7 | 3 | N/S | <4 | <4 | 1493 | 256 | 2 | 0.3 | 18.3 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-01 | 2.31 | 7.4 | 9.7 | N/S | N/S | N/S | 8 | 6 | 1704 | 282 | 2 | 0.1 | 18.72 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-02 | 2.29 | 7.4 | 8.9 | N/S | N/S | N/S | 5 | 4 | 1634 | 220 | 2 | 0.1 | 16.45 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-03 | 2.26 | 7.4 | 9.5 | 7 | 3 | N/S | 7 | 6 | 1610 | 196 | 2 | <0.1 | 18.82 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-04 | 2.35 | 7.4 | 9.6 | 5 | 3 | <5 | 6 | 6 | 1604 | 232 | 2 | 0.1 | 19.61 | 2.7 | 0.005 | <5 | N/S | 0.9 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S
2015-05-05 | 3.18 | 7.4 | 10 | 6 | 3 | N/S | 7 | 4 | 1237 | 174 | 2 | 0.1 | 15.3 | 2.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.01 | 0.1 | <0.1 | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 83 | 36 | 357 | 0.7 | 5
2015-05-06 | 3.5 | 7.3 | 9.5 | 5 | 2 | N/S | 6 | 6 | 1229 | 184 | 2 | 0.1 | 14.07 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-07 | 3.25 | 7.4 | 9.3 | T/X | T/X | N/S | 6 | 4 | 1318 | 214 | 2 | 0.1 | 15.38 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-08 | 2.5 | 7.4 | 9 | N/S | N/S | N/S | 6 | 4 | 1510 | 208 | 2 | <0.1 | 15.92 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-09 | 4.09 | 7.3 | 8.8 | N/S | N/S | N/S | 7 | 5 | 1080 | 152 | 2 | <0.1 | 10.28 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-10 | 4.27 | 7.4 | 7.5 | 6 | 3 | N/S | 6 | 5 | 810 | 102 | 1 | <0.1 | 9.71 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-11 | 4.24 | 7.4 | 8.4 | 5 | 2 | <5 | 8 | 6 | 858 | 88 | 1 | <0.1 | 12.26 | 1.3 | <0.005 | <5 | N/S | 0.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-05-12 | 3.79 | 7.2 | 7 | 7 | 3 | N/S | 6 | 6 | 1192 | 172 | 1 | 0.1 | 12.13 | 1.4 | N/S | N/S | N/S | N/S | 3200 | <0.05 | 0.037 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.008 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 90 | 39 | 386 | <0.5 | 4
2015-05-13 | 3.08 | 7.4 | 9.9 | T/X | T/X | N/S | 7 | <4 | 1361 | 202 | 1 | 0.1 | 14.22 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-14 | 2.42 | 7.4 | 9.4 | 7 | 3 | N/S | 6 | 4 | 1483 | 262 | 1 | 0.1 | 16.07 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-15 | 2.76 | 7.4 | 9.4 | N/S | N/S | N/S | 6 | 4 | 1452 | 168 | 1 | 0.1 | 16.75 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-16 | 2.6 | 7.4 | 9.9 | N/S | N/S | N/S | 4 | <4 | 1264 | 134 | 1 | 0.1 | 14.59 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-17 | 3.08 | 7.4 | 9.9 | 6 | 3 | N/S | 4 | 4 | 1166 | 124 | 1 | <0.1 | 14.53 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-18 | 2.69 | 7.3 | 9.1 | 7 | 4 | <5 | 6 | 4 | 1281 | 160 | 1 | 0.1 | 15.89 | 2.1 | 0.005 | <5 | N/S | 0.8 | 2200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-05-19 | 2.2 | 7.4 | 10 | 6 | 3 | N/S | 5 | 4 | 1401 | 224 | 2 | 0.1 | 17.12 | 2.3 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.047 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 113 | 45 | 468 | 1.4 | 5
2015-05-20 | 2.17 | 7.4 | 9.8 | 8 | 3 | N/S | 7 | 6 | 1349 | 208 | 2 | 0.1 | 19.99 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-21 | 2.15 | 7.4 | 9.9 | 8 | 4 | N/S | 7 | 6 | 1424 | 228 | 2 | 0.1 | 19.54 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-22 | 2.09 | 7.3 | 7.2 | N/S | N/S | N/S | 11 | 8 | 1370 | 222 | 2 | 0.2 | 19.68 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-23 | 2.03 | 7.2 | 7.2 | N/S | N/S | N/S | 10 | 10 | 1370 | 184 | 3 | 0.3 | 19.1 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-24 | 2.04 | 7.3 | 7.3 | 9 | 4 | N/S | 10 | 8 | 1326 | 216 | 2 | 0.1 | 18.94 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-25 | 2.72 | 7.3 | 7.7 | 9 | 3 | <5 | 8 | 6 | 1132 | 168 | 2 | 0.1 | 15.2 | 2.2 | <0.005 | <5 | N/S | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-26 | 2.68 | 7.3 | 7.6 | 16 | 8 | N/S | 31 | 27 | 1146 | 214 | 4 | 0.2 | 13.37 | 2.2 | N/S | N/S | N/S | N/S | 6000 | <0.05 | 0.04 | <0.001 | <0.005 | 0.018 | 0.3 | N/S | <0.02 | 0.036 | <0.2 | <0.005 | 0.023 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 83 | 36 | 356 | 0.8 | 6
2015-05-27 | 3.59 | 7.2 | 7.3 | 19 | 7 | N/S | 21 | 16 | 1112 | 172 | 3 | 0.2 | 11.78 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-28 | 2.81 | 7.3 | 9 | 14 | 6 | N/S | 19 | 16 | 1267 | 168 | 2 | 0.2 | 14.13 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-05-29 | 2.29 | 7.4 | 9.6 | N/S | N/S | N/S | 10 | 8 | 1482 | 180 | 2 | 0.3 | 15.89 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-30 | 2.29 | 7.3 | 8.1 | N/S | N/S | N/S | 48 | 41 | 1408 | 180 | 4 | 0.2 | 17.37 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-05-31 | 3.95 | 7.2 | 9.3 | 17 | 12 | N/S | 32 | 28 | 1135 | 140 | 3 | 0.1 | 12.05 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-01 | 2.95 | 7.2 | 9.8 | 11 | 6 | <5 | 13 | 9 | 1303 | 160 | 2 | 0.1 | 12.32 | 1.5 | <0.005 | <5 | N/S | 0.6 | 4500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-06-02 | 2.92 | 7.3 | 9.3 | 10 | 4 | N/S | 12 | 9 | 1142 | 186 | 3 | 0.3 | 15.49 | 2.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.044 | <0.001 | <0.005 | 0.016 | 0.1 | 0.1 | <0.02 | 0.018 | <0.2 | <0.005 | 0.013 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 99 | 41 | 415 | 1 | 5
2015-06-03 | 2.23 | 7.4 | 9 | 10 | 5 | N/S | 9 | 7 | 1244 | 190 | 4 | 0.2 | 17.94 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-04 | 2.21 | 7.4 | 7 | 9 | 3 | N/S | 8 | 8 | 1250 | 186 | 2 | 0.2 | 19.55 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-05 | 2.15 | 7.3 | 8.9 | N/S | N/S | N/S | 9 | 7 | 1202 | 230 | 2 | 0.3 | 21.33 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-06 | 2.12 | 7.3 | 7.5 | N/S | N/S | N/S | 8 | 7 | 1466 | 266 | 3 | 0.5 | 19.61 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-07 | 3.03 | 7.3 | 7.8 | 10 | 5 | N/S | 11 | 8 | 1326 | 208 | 3 | 0.4 | 16.43 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-08 | 3.32 | 7.3 | 7 | 7 | 3 | <5 | 6 | 6 | 1190 | 150 | 2 | 0.2 | 10.97 | 1.5 | <0.005 | <5 | N/S | 0.6 | 4700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-06-09 | 2.6 | 7.4 | 6.5 | 8 | 4 | N/S | 6 | 6 | 1389 | 278 | 2 | 0.3 | 14.81 | 2 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.046 | <0.001 | <0.005 | 0.02 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 102 | 41 | 424 | 0.5 | 5
2015-06-10 | 2.75 | 7.3 | 9.4 | 8 | 4 | N/S | 7 | 6 | 1219 | 188 | 2 | 0.3 | 16.09 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-11 | 2.7 | 7.3 | 8.4 | 9 | 4 | N/S | 10 | 6 | 1264 | 244 | 3 | 0.7 | 16.12 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-12 | 2.21 | 7.4 | 7.2 | N/S | N/S | N/S | 8 | 7 | 1292 | 266 | 3 | 0.5 | 17.75 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-13 | 2.24 | 7.3 | 9.2 | N/S | N/S | N/S | 9 | 8 | 1164 | 224 | 2 | 0.2 | 18.6 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-14 | 4.14 | 7.2 | 8.5 | 8 | 5 | N/S | 13 | 11 | 882 | 186 | 1 | 0.2 | 10.65 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-15 | 4.28 | 7.2 | 9.7 | 8 | 4 | <5 | 10 | 9 | 830 | 146 | 1 | <0.1 | 9.14 | 1.1 | <0.005 | <5 | N/S | 0.5 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-06-16 | 4.31 | 7.2 | 9.1 | 7 | 3 | N/S | 13 | 8 | 818 | 120 | 1 | 0.1 | 8.9 | 1.1 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.031 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 75 | 33 | 324 | <0.5 | 5
2015-06-17 | 4.22 | 7.3 | 9 | 8 | 3 | N/S | 11 | 8 | 1073 | 206 | 1 | <0.1 | 9.93 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-18 | 3.82 | 7.1 | 9.3 | 8 | 3 | N/S | 10 | 8 | 1098 | 176 | 2 | 0.1 | 12.23 | 1.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-19 | 2.79 | 7.3 | 9.8 | N/S | N/S | N/S | 10 | 7 | 1122 | 178 | 2 | 0.2 | 14.56 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-20 | 2.76 | 7.4 | 8.7 | N/S | N/S | N/S | 10 | 9 | 1495 | 242 | 2 | 0.3 | 15.82 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-21 | 3.89 | 7.3 | 8.1 | 7 | 4 | N/S | 12 | 10 | 1244 | 204 | 2 | 0.2 | 12.73 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-22 | 3.09 | 7.4 | 7 | 7 | 3 | <5 | 9 | 8 | 1322 | 170 | 2 | 0.2 | 12.91 | 1.6 | <0.005 | <5 | N/S | 0.7 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-06-23 | 2.92 | 7.4 | 5.7 | 6 | 3 | N/S | 10 | 8 | 1273 | 166 | 2 | 0.2 | 15.01 | 1.9 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.039 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.019 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 93 | 38 | 390 | 0.7 | 4
2015-06-24 | 2.87 | 7.3 | 9 | 5 | <2 | N/S | 8 | 6 | 1360 | 204 | 2 | 0.2 | 16.18 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-25 | 2.34 | 7.4 | 9 | 5 | 2 | N/S | 7 | 4 | 1301 | 298 | 2 | 0.3 | 16.62 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-26 | 2.42 | 7.4 | 8.8 | N/S | N/S | N/S | 7 | 6 | 1214 | 192 | 2 | 0.2 | 17.45 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-27 | 3.82 | 7.2 | 9.8 | N/S | N/S | N/S | 7 | 6 | 1014 | 170 | 2 | 0.1 | 12.71 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-28 | 2.65 | 7.4 | 9.9 | 5 | 2 | N/S | 4 | <4 | 1120 | 184 | 2 | 0.2 | 14.15 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-06-29 | 3.46 | 7.4 | 9.1 | 8 | 3 | <5 | 7 | 6 | 1204 | 270 | 2 | 0.2 | 14.39 | 2 | <0.005 | <5 | N/S | 0.7 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-06-30 | 3.47 | 7.4 | 8.6 | 5 | 2 | N/S | 7 | 5 | 1082 | 208 | 2 | 0.2 | 12.14 | 1.8 | N/S | N/S | N/S | N/S | N/S | <0.05 | 0.036 | 0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.01 | <0.2 | <0.005 | 0.016 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 84 | 34 | 349 | <0.5 | 4
2015-07-01 | 2.73 | 7.5 | 9 | 8 | 2 | N/S | 10 | 7 | 1126 | 192 | 4 | 0.2 | 14.2 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-02 | 2.62 | 7.5 | 9.6 | 5 | <2 | N/S | 6 | 6 | 1200 | 236 | 2 | 0.2 | 17.11 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-03 | 2.91 | 7.4 | 7 | N/S | N/S | N/S | 6 | 6 | 1331 | 240 | 2 | 0.3 | 17.89 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-04 | 2.38 | 7.5 | 8.7 | N/S | N/S | N/S | 6 | 6 | 1348 | 230 | 2 | 0.4 | 17.85 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-05 | 1.98 | 7.4 | 7.7 | 6 | 5 | N/S | 6 | 5 | 1409 | 278 | 1 | 0.3 | 18.91 | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-06 | 1.97 | 7.5 | 6.1 | 13 | 7 | <5 | 25 | 18 | 1140 | 262 | 1 | 0.1 | 13.83 | 0.6 | <0.005 | <5 | N/S | 0.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 7 | N/S | N/S | N/S | N/S | N/S
2015-07-07 | 4.18 | 7.4 | 7.8 | 10 | 5 | N/S | 15 | 13 | 840 | 136 | 2 | 0.1 | 10.58 | 1.7 | N/S | N/S | 155.6 | N/S | 13000 | <0.05 | 0.034 | 0.001 | <0.005 | 0.01 | 0.2 | <0.1 | <0.02 | 0.015 | <0.2 | <0.005 | 0.016 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 72 | 28 | 296 | 2.7 | 5
2015-07-08 | 4.27 | 7.3 | 7.6 | 7 | 4 | N/S | 5 | 5 | 1106 | 142 | 2 | 0.1 | 10.66 | 1.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-09 | 3.25 | 7.2 | 9.7 | 14 | 6 | N/S | 22 | 19 | 1469 | 196 | 3 | 0.3 | 12.31 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-10 | 2.77 | 7.2 | 7.5 | N/S | N/S | N/S | 4 | <4 | 1512 | 178 | 3 | 0.3 | 14.25 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-11 | 2.33 | 7.4 | 8.6 | N/S | N/S | N/S | 7 | 5 | 1464 | 196 | 3 | 0.2 | 16.83 | 2.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-12 | 2.31 | 7.4 | 9.5 | 8 | 4 | N/S | 6 | 4 | 1218 | 134 | 3 | 0.9 | 17.85 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-13 | 3.57 | 7.3 | 9.5 | N/A | 11 | <5 | 40 | 32 | 938 | 126 | 6 | 1.9 | 13.66 | 2.7 | <0.005 | 8 | N/S | 0.7 | 6100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 8 | N/S | N/S | N/S | N/S | N/S
2015-07-14 | 3.3 | 7.3 | 8.8 | 11 | 4 | N/S | 14 | 11 | 820 | 120 | 3 | 0.3 | 11.58 | 1.7 | N/S | N/S | 192 | N/S | N/S | <0.05 | 0.027 | <0.001 | <0.005 | 0.008 | 0.2 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 64 | 29 | 281 | 0.9 | 5
2015-07-15 | 2.73 | 7.4 | 8.1 | 7 | 3 | N/S | 7 | 7 | 1240 | 220 | 3 | 0.3 | 14.87 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-16 | 2.67 | 7.6 | 8.1 | T/X | T/X | N/S | 10 | 7 | 1444 | 294 | 2 | 0.2 | 15.83 | 2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-17 | 4.17 | 7.1 | 8.6 | N/S | N/S | N/S | 13 | 10 | 1062 | 204 | 3 | 0.1 | 12.02 | 1.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-18 | 3.59 | 7.2 | 7.4 | N/S | N/S | N/S | 5 | 4 | 1098 | 208 | 3 | 0.2 | 12.34 | 1.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-19 | 2.4 | 7.1 | 8.1 | 4 | 2 | N/S | <4 | <4 | 1192 | 198 | 3 | 0.2 | 14.68 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-20 | 2.94 | 7.1 | 9.2 | 6 | 4 | <5 | 7 | 5 | 1182 | 148 | 3 | 0.2 | 16.41 | 2.2 | <0.005 | 6 | N/S | 0.8 | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-07-21 | 2.45 | 7.4 | 8.9 | 11 | 6 | N/S | 10 | 8 | 1338 | 240 | 4 | 0.3 | 14.68 | 2.6 | N/S | N/S | 414 | N/S | N/S | <0.05 | 0.043 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | 0.013 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 98 | 37 | 399 | <0.5 | 6
2015-07-22 | 2.34 | 7.5 | 9.7 | T/X | T/X | N/S | 10 | 8 | 1422 | 226 | 4 | 0.8 | 13.83 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-23 | 1.94 | 7.2 | 10 | 6 | 4 | N/S | 7 | 7 | 1492 | 238 | 2 | 0.3 | 16.71 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-24 | 2.28 | 7.3 | 9.6 | N/S | N/S | N/S | 6 | 6 | 1546 | 268 | 2 | 0.2 | 18.46 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-25 | 2.17 | 7.4 | 9 | N/S | N/S | N/S | 7 | 6 | 1482 | 246 | 2 | 0.2 | 19.38 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-26 | 2.38 | 7.6 | 8.7 | 7 | 3 | N/S | 8 | 7 | 1469 | 268 | 2 | 0.2 | 19.33 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-27 | 2.31 | 7.3 | 8.5 | T/X | T/X | <5 | 6 | 6 | 1382 | 244 | 3 | 0.2 | 18.03 | 2.8 | <0.005 | 7 | N/S | T/X | 6600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-07-28 | 1.88 | 7.3 | 8.5 | 5 | 4 | N/S | 7 | 5 | 1318 | 226 | 2 | 0.3 | 16.01 | 2.8 | N/S | N/S | 382 | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 112 | 43 | 456 | 0.7 | 6
2015-07-29 | 2.27 | 7.3 | 8.5 | 8 | 5 | N/S | 5 | 5 | 1200 | 198 | 2 | 0.5 | 16.45 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-30 | 2.2 | 7.5 | 8 | T/X | T/X | N/S | 4 | 4 | 1118 | 166 | 3 | 0.5 | 15.83 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-07-31 | 1.98 | 7.1 | 9.1 | N/S | N/S | N/S | 16 | 10 | 1506 | 310 | 2 | 0.3 | 17.27 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-01 | 2.04 | 7.1 | 8.9 | N/S | N/S | N/S | 6 | 4 | 1794 | 378 | 2 | 0.7 | 17.67 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-02 | 2 | 7.2 | 8 | 14 | 6 | N/S | 24 | 19 | 1845 | 388 | 4 | 1.1 | 17.36 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-03 | 2.71 | 7.2 | 5.9 | 10 | 5 | <5 | 12 | 10 | 1516 | 324 | 3 | 0.4 | 14.88 | 2.7 | <0.005 | 8 | N/S | 0.8 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-08-04 | 2.23 | 7.4 | 9.2 | 10 | 5 | N/S | 10 | 7 | 1448 | 252 | 3 | 0.6 | 16.02 | 3 | N/S | N/S | 497 | N/S | N/S | <0.05 | 0.044 | <0.001 | <0.005 | 0.006 | 0.1 | <0.1 | <0.02 | 0.038 | <0.2 | <0.005 | 0.036 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 114 | 43 | 463 | 0.6 | 6
2015-08-05 | 1.98 | 7.5 | 9.1 | 8 | 4 | N/S | 7 | 5 | 1561 | 300 | 2 | 0.6 | 18.54 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-06 | 1.93 | 7.4 | 8.4 | 5 | 3 | N/S | 7 | 6 | 1407 | 240 | 3 | 0.7 | 19.06 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-07 | 1.91 | 7.4 | 8.8 | N/S | N/S | N/S | 4 | <4 | 1336 | 226 | 3 | 0.6 | 20.16 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-08 | 1.92 | 7.4 | 9.4 | N/S | N/S | N/S | 9 | 7 | 1960 | 414 | 2 | 0.8 | 19.83 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-09 | 2.05 | 7.3 | 8.6 | 9 | 5 | N/S | 5 | 5 | 2197 | 452 | 3 | 1.1 | 18.9 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-10 | 2.07 | 7.5 | 8 | 6 | 4 | <5 | 8 | 6 | 2174 | 348 | 3 | 0.7 | 18.67 | 3 | <0.005 | 6 | N/S | 1.1 | 86000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-08-11 | 2.19 | 7.5 | 8.4 | 7 | 4 | N/S | 8 | 6 | 1920 | 304 | 3 | 0.4 | 17.38 | 2.9 | N/S | N/S | 275 | N/S | N/S | <0.05 | 0.047 | 0.001 | <0.005 | 0.005 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | 0.012 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 124 | 44 | 494 | <0.5 | 5
2015-08-12 | 2.01 | 7.4 | 8.3 | 6 | 3 | N/S | 6 | 5 | 1887 | 334 | 2 | 0.5 | 18.77 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-13 | 1.98 | 7.4 | 8.3 | 8 | 4 | N/S | 8 | 6 | 1670 | 256 | 2 | 0.5 | 18.7 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-14 | 2.04 | 7.4 | 8.6 | N/S | N/S | N/S | 13 | 10 | 1588 | 294 | 3 | 0.4 | 19.37 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-15 | 2.35 | 7.4 | 8 | N/S | N/S | N/S | 13 | 10 | 1574 | 320 | 3 | 0.4 | 16.31 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-16 | 1.98 | 7.3 | 8.2 | T/X | T/X | N/S | 12 | 9 | 1698 | 342 | 3 | 0.8 | 16.63 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-17 | 2.04 | 7.3 | 7.4 | 12 | 7 | <5 | 18 | 16 | 1700 | 322 | 4 | 0.4 | 17.79 | 3.2 | <0.005 | 5 | N/S | 1 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-08-18 | 3.12 | 7.4 | 7.2 | 10 | 6 | N/S | 13 | 11 | 1203 | 200 | 3 | 0.4 | 14.29 | 2.5 | N/S | N/S | 393.2 | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.01 | 5.9 | N/S | <0.02 | 0.049 | <0.2 | <0.005 | 0.015 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 89 | 34 | 363 | 0.7 | 6
2015-08-19 | 3.52 | 7.2 | 7.9 | 7 | 4 | N/S | 5 | 4 | 988 | 150 | 2 | 0.4 | 10.99 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-20 | 2.5 | 7.4 | 9.3 | 6 | 5 | N/S | 10 | 8 | 1097 | 212 | 3 | 0.3 | 14.69 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-21 | 2.51 | 7.4 | 8.5 | N/S | N/S | N/S | 9 | 7 | 1176 | 170 | 3 | 0.3 | 17.13 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-22 | 1.97 | 7.4 | 8.3 | N/S | N/S | N/S | 7 | 6 | 1180 | 194 | 3 | 0.4 | 19.45 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-23 | 2.04 | 7.4 | 8.2 | 10 | 5 | N/S | 9 | 7 | 1218 | 214 | 4 | 0.6 | 20.65 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-24 | 2.11 | 7.4 | 8.8 | 13 | 6 | <5 | 18 | 14 | 1166 | 150 | 3 | 0.6 | 19.69 | 3.4 | <0.005 | <5 | N/S | 1.1 | 53000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-08-25 | 1.4 | 7.6 | 7.7 | 7 | 3 | N/S | 11 | 9 | 1076 | 124 | 3 | 0.5 | 19.05 | 3.1 | N/S | N/S | 293 | N/S | N/S | <0.05 | 0.031 | 0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.02 | <0.2 | <0.005 | 0.032 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 89 | 33 | 360 | <0.5 | 6
2015-08-26 | 1.98 | 7.5 | 9.8 | 10 | 6 | N/S | 10 | 8 | 1032 | 152 | 2 | 0.3 | 20.58 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-27 | 2.3 | 7.3 | 8 | 10 | 6 | N/S | 9 | 7 | 1256 | 180 | 3 | 0.3 | 20.66 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-28 | 2.28 | 7.4 | 8.7 | N/S | N/S | N/S | 8 | 8 | 1644 | 338 | 3 | 0.3 | 20.6 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-29 | 1.88 | 7.4 | 6.5 | N/S | N/S | N/S | 8 | 8 | 1630 | 340 | 3 | 0.5 | 20.74 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-30 | 1.85 | 7.5 | 8.8 | 13 | 5 | N/S | 14 | 12 | 1221 | 214 | 3.97 | 0.6 | 21.14 | 3.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-08-31 | 2.12 | 7.5 | 7.2 | T/X | T/X | <5 | 12 | 10 | 1246 | 230 | 3 | 0.4 | 21.25 | 3.5 | <0.005 | 5 | N/S | 1.1 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-09-01 | 1.77 | 7.5 | 7 | 8 | 4 | N/S | 10 | 8 | 1190 | 148 | 3 | 0.3 | 21.39 | 3.5 | N/S | N/S | 328.2 | N/S | N/S | <0.05 | 0.04 | 0.001 | <0.005 | 0.014 | 0.1 | <0.1 | <0.02 | 0.026 | <0.2 | <0.005 | 0.024 | 0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 97 | 36 | 391 | 0.8 | 6
2015-09-02 | 1.9 | 7.5 | 9 | 8 | 3 | N/S | 8 | 8 | 1641 | 322 | 3 | 0.4 | 22.61 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-03 | 1.86 | 7.5 | 7.9 | 7 | 4 | N/S | 8 | 5 | 1832 | 354 | 2 | 0.4 | 22.24 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-04 | 1.9 | 7.4 | 8.5 | N/S | N/S | N/S | 10 | 8 | 1706 | 318 | 2 | 0.4 | 21.07 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-05 | 1.92 | 7.5 | 7.2 | N/S | N/S | N/S | 5 | <4 | 1537 | 294 | 2 | 0.5 | 21.2 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-06 | 1.91 | 7.4 | 7.4 | 8 | 5 | N/S | 10 | 7 | 1358 | 232 | 3 | 0.5 | 21.33 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-07 | 2.03 | 7.5 | 8.7 | 9 | 4 | <5 | 8 | 7 | 1260 | 194 | 4 | 1 | 20.16 | 3.6 | 0.005 | 6 | N/S | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-08 | 2 | 7.6 | 5 | 7 | 4 | N/S | 8 | 6 | 1092 | 144 | 3 | 0.4 | 19.26 | 3.1 | N/S | N/S | 316.6 | N/S | 83000 | <0.05 | 0.033 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.018 | <0.2 | <0.005 | 0.01 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 88 | 33 | 357 | <0.5 | 6
2015-09-09 | 2.49 | 7.4 | 9.2 | 7 | 4 | N/S | 9 | 8 | 1182 | 240 | 3 | 0.2 | 16.14 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-10 | 2.63 | 7.4 | 9 | 6 | 4 | N/S | 7 | <4 | 1347 | 270 | 3 | 0.2 | 16.62 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-11 | 2.68 | 7.5 | 8.6 | N/S | N/S | N/S | 11 | 7 | 1543 | 232 | 3 | 0.3 | 17.46 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-12 | 2.65 | 7.5 | 6.8 | N/S | N/S | N/S | 11 | 7 | 1464 | 192 | 3 | 0.4 | 18.17 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-13 | 2.29 | 7.5 | 7.8 | 7 | 3 | N/S | 5 | 5 | 1288 | 172 | 4 | 0.7 | 18.85 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-14 | 1.8 | 7.5 | 6.7 | 6 | 3 | <5 | 5 | 4 | 1212 | 168 | 4 | 0.5 | 21.5 | 3.4 | <0.005 | <5 | N/S | 1 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-09-15 | 1.7 | 7.5 | 6.8 | 5 | 3 | N/S | 4 | 4 | 1344 | 188 | 4 | 0.4 | 22.43 | 3.4 | N/S | N/S | 411.6 | N/S | N/S | <0.05 | 0.035 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 104 | 39 | 421 | 0.7 | 7
2015-09-16 | 1.85 | 7.5 | 8.5 | 8 | 4 | N/S | 6 | 6 | 1374 | 244 | 5 | 0.5 | 22.33 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-17 | 1.65 | 7.6 | 6.7 | T/X | T/X | N/S | 6 | 5 | 1234 | 198 | 5 | 0.6 | 22.27 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-18 | 3.36 | 7.4 | 6.8 | N/S | N/S | N/S | 11 | 10 | 852 | 150 | 4 | 0.2 | 14.35 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-19 | 4.3 | 7.4 | 8.5 | N/S | N/S | N/S | 9 | 8 | 730 | 144 | 3 | 0.1 | 8.73 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-20 | 4.24 | 7.4 | 9.1 | 4 | 3 | N/S | 7 | 7 | 996 | 182 | 3 | 0.2 | 10.33 | 1.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-21 | 2.83 | 7.4 | 5.7 | 6 | 3 | <5 | 12 | 11 | 1218 | 180 | 4 | 0.2 | 13.16 | 1.7 | <0.005 | <5 | N/S | 0.7 | 23000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-09-22 | 2.5 | 7.6 | 6.2 | 6 | 3 | N/S | 6 | 6 | 1334 | 216 | 3 | 0.3 | 16.39 | 2.1 | N/S | N/S | 429.3 | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.016 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 100 | 37 | 403 | 0.6 | 5
2015-09-23 | 2.46 | 7.6 | 6.3 | 8 | 4 | N/S | 13 | 12 | 1436 | 196 | 4 | 0.3 | 18.43 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-24 | 2.46 | 7.5 | 6.8 | 9 | 3 | N/S | 5 | 5 | 1474 | 216 | 3 | 0.3 | 17.87 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-25 | 2.02 | 7.5 | 7 | N/S | N/S | N/S | 5 | 5 | 1527 | 292 | 3 | 0.3 | 20.2 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-26 | 2.14 | 7.6 | 6.5 | N/S | N/S | N/S | 7 | 5 | 1475 | 270 | 3 | 0.3 | 20.24 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-27 | 2.14 | 7.6 | 6 | 5 | 3 | N/S | 4 | 4 | 1356 | 244 | 3 | 0.3 | 19.78 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-09-28 | 2.18 | 7.6 | 6.5 | 6 | 2 | <5 | 6 | 4 | 1120 | 120 | 3 | 0.3 | 19.02 | 3 | <0.005 | <5 | N/S | 1 | 12000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-09-29 | 2.16 | 7.5 | 8.7 | 4 | 2 | N/S | 4 | 5 | 1073 | 128 | 3 | 0.3 | 19.45 | 3 | N/S | N/S | 306.2 | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.015 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 93 | 34 | 371 | <0.5 | 5
2015-09-30 | 1.93 | 7.6 | 7.4 | 3 | 2 | N/S | 4 | 4 | 1047 | 136 | 3 | 0.3 | 21.91 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-01 | 1.79 | 7.6 | 9.2 | 4 | <2 | N/S | 10 | <4 | 1027 | 106 | 3 | 0.3 | 22.24 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-02 | 1.78 | 7.5 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1072 | 144 | 2 | 0.3 | 22.73 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-03 | 1.93 | 7.5 | 7.4 | N/S | N/S | N/S | 4 | <4 | 1050 | 128 | 3 | 0.3 | 23.58 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-04 | 1.96 | 7.5 | 8.1 | 3 | <2 | N/S | <4 | <4 | 1053 | 124 | 3 | 0.3 | 22.98 | 3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-05 | 1.82 | 7.6 | 6.3 | 4 | 2 | <5 | 6 | 6 | 1061 | 132 | 3 | 0.3 | 22.57 | 3.1 | <0.005 | <5 | N/S | 1.1 | 2400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-10-06 | 1.79 | 7.5 | 7 | 5 | 2 | N/S | 5 | 4 | 1052 | 134 | 2 | 0.3 | 22.53 | 3.3 | N/S | N/S | 325.8 | N/S | N/S | <0.05 | 0.028 | <0.001 | <0.005 | <0.005 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.017 | <0.001 | 0.01 | <0.05 | <0.001 | <0.1 | N/S | 84 | 31 | 338 | <0.5 | 5
2015-10-07 | 1.74 | 7.6 | 6.2 | 5 | 3 | N/S | 5 | 4 | 1070 | 180 | 3 | 0.3 | 24.12 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-08 | 1.83 | 7.5 | 6.9 | 7 | 3 | N/S | 6 | 6 | 1037 | 140 | 2 | 0.2 | 24.79 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-09 | 1.74 | 7.2 | 9 | N/S | N/S | N/S | 7 | 7 | 1185 | 212 | 3 | 0.2 | 23.48 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-10 | 1.83 | 7.5 | 7.8 | N/S | N/S | N/S | 10 | 8 | 1240 | 234 | 3 | 0.2 | 23.58 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-11 | 1.86 | 7.5 | 7.4 | 5 | 3 | N/S | 12 | 10 | 1130 | 174 | 3 | 0.2 | 22.66 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-12 | 1.78 | 7.4 | 8 | T/X | T/X | <5 | 13 | 9 | 1220 | 194 | 3 | 0.2 | 22.28 | 3.3 | <0.005 | <5 | N/S | 1.2 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-10-13 | 1.69 | 7.4 | 9 | 9 | 3 | N/S | 14 | 10 | 1202 | 196 | 2 | 0.2 | 22.45 | 3.4 | N/S | N/S | 320.8 | N/S | N/S | <0.05 | 0.036 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | 0.04 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 91 | 32 | 361 | 1.2 | 5
2015-10-14 | 1.84 | 7.4 | 9.7 | 7 | 3 | N/S | 12 | 9 | 1198 | 122 | 3 | 0.3 | 22.53 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-15 | 1.69 | 7.5 | 7.4 | 7 | 3 | N/S | 12 | 10 | 1210 | 152 | 3 | 0.2 | 24.16 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-16 | 1.66 | 7.5 | 7.5 | N/S | N/S | N/S | 8 | 6 | 1340 | 238 | 2 | 0.2 | 25.72 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-17 | 1.79 | 7.4 | 7.9 | N/S | N/S | N/S | 6 | 4 | 1406 | 246 | 2 | 0.3 | 25.67 | 3.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-18 | 1.92 | 7.4 | 7.4 | 7 | 3 | N/S | 9 | 6 | 1292 | 194 | 2 | 0.3 | 24.72 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-19 | 1.69 | 7.5 | 6.8 | 5 | 2 | <5 | 8 | 5 | 1268 | 190 | 2 | 0.2 | 24.13 | 3.3 | <0.005 | 6 | N/S | 1.2 | 9100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-10-20 | 1.7 | 7.4 | 7.1 | 4 | <2 | N/S | 6 | 4 | 1126 | 110 | 3 | 0.2 | 23.64 | 3.4 | N/S | N/S | 329.1 | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 86 | 30 | 340 | <0.5 | 5
2015-10-21 | 1.71 | 7.5 | 6.2 | 6 | 3 | N/S | 8 | 8 | 1220 | 190 | 2 | 0.2 | 24.5 | 3.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-22 | 1.78 | 7.5 | 5.9 | 7 | 3 | N/S | 8 | 4 | 1408 | 258 | 3 | 0.3 | 26.16 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-23 | 1.83 | 7.4 | 7 | N/S | N/S | N/S | 14 | 5 | 1543 | 314 | 3 | 0.2 | 24.37 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-24 | 1.96 | 7.5 | 7.5 | N/S | N/S | N/S | 10 | 6 | 1486 | 276 | 3 | 0.2 | 23.14 | 3.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-25 | 1.95 | 7.4 | 6.7 | 9 | 4 | N/S | 10 | 6 | 1456 | 258 | 3 | 0.4 | 22.19 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-26 | 1.99 | 7.5 | 7.6 | 9 | 4 | <5 | 12 | 8 | 1673 | 402 | 3 | 0.3 | 22.18 | 3.8 | <0.005 | 5 | N/S | 1.1 | 6700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-10-27 | 1.93 | 7.4 | 6.7 | 9 | 3 | N/S | 12 | 10 | 1414 | 258 | 3 | 0.2 | 22.99 | 3.7 | N/S | N/S | 481.8 | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.023 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 91 | 33 | 361 | <0.5 | 6
2015-10-28 | 2.54 | 7.4 | 7.1 | 5 | 3 | N/S | 10 | 7 | 1078 | 140 | 2 | 0.1 | 17.98 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-29 | 2.6 | 7.4 | 7.6 | 3 | <2 | N/S | <4 | <4 | 1054 | 74 | 2 | 0.1 | 17.23 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-30 | 2.55 | 7.4 | 7.7 | N/S | N/S | N/S | 14 | 10 | 1306 | 206 | 3 | 0.2 | 18.51 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-10-31 | 2.54 | 7.4 | 6.5 | N/S | N/S | N/S | 17 | 12 | 1124 | 176 | 3 | 0.2 | 17.31 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-01 | 3.7 | 7.2 | 7 | 9 | 4 | N/S | 15 | 11 | 830 | 122 | 3 | 0.1 | 12.53 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-02 | 2.34 | 7.4 | 6.7 | 7 | 4 | <5 | 11 | 7 | 990 | 126 | 2 | 0.2 | 15.86 | 2.1 | <0.005 | <5 | N/S | 0.8 | 990 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-11-03 | 2.5 | 7.4 | 7.3 | 8 | 4 | N/S | 12 | 7 | 1106 | 136 | 3 | 0.2 | 18.4 | 2.6 | N/S | N/S | 334.6 | N/S | N/S | <0.05 | 0.032 | <0.001 | <0.005 | 0.014 | 0.1 | <0.1 | <0.02 | 0.013 | <0.2 | <0.005 | 0.023 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 79 | 29 | 318 | 4.3 | 6
2015-11-04 | 2.27 | 7.3 | 6.7 | T/X | T/X | N/S | 13 | 10 | 1218 | 166 | 3 | 0.3 | 19.62 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-05 | 2 | 7.4 | 6.7 | 8 | 5 | N/S | 13 | 11 | 1294 | 170 | 5 | 0.2 | 20.62 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-06 | 2.22 | 7.5 | 8 | N/S | N/S | N/S | 11 | 8 | 1117 | 180 | 2 | 0.1 | 18.54 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-07 | 2.54 | 7.4 | 7.6 | N/S | N/S | N/S | 15 | 12 | 1068 | 178 | 3 | 0.1 | 16.95 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-08 | 2.43 | 7.4 | 7.8 | 9 | 6 | N/S | 10 | 8 | 1136 | 154 | 3 | 0.1 | 18.19 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-09 | 2.28 | 7.5 | 7.8 | 9 | 6 | <5 | 21 | 16 | 1314 | 228 | 6 | 0.1 | 18.97 | 3.3 | <0.005 | <5 | N/S | 1 | 1600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-11-10 | 1.82 | 7.4 | 9.7 | 10 | 5 | N/S | 18 | 13 | 1243 | 160 | 3 | 0.2 | 18.63 | 3.1 | N/S | N/S | 399 | N/S | N/S | <0.05 | 0.036 | 0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.016 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 91 | 33 | 361 | T/X | 5
2015-11-11 | 1.83 | 7.5 | 6.6 | 12 | 8 | N/S | 27 | 20 | 1086 | 138 | 3 | 0.1 | 18.69 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-12 | 3.3 | 7.4 | 7.8 | T/X | T/X | N/S | 47 | 40 | 822 | 126 | 5 | 0.1 | 15.38 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-13 | 2.43 | 7.4 | 8 | N/S | N/S | N/S | 17 | 14 | 832 | 114 | 3 | <0.1 | 12.46 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-14 | 2.46 | 7.4 | 8.4 | N/S | N/S | N/S | 4 | 4 | 980 | 154 | 3 | 0.1 | 15.74 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-15 | 2.44 | 7.4 | 7.6 | 8 | 4 | N/S | 9 | 8 | 1044 | 172 | 3 | 0.2 | 17.44 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-16 | 2.44 | 7.4 | 7.6 | 3 | <2 | <5 | 5 | <4 | 1123 | 134 | 3 | 0.2 | 18.81 | 2.5 | 0.005 | 7 | N/S | 1 | 9500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-11-17 | 2.53 | 7.4 | 8.9 | 12 | 7 | N/S | 27 | 22 | 992 | 128 | 4 | 0.1 | 16.82 | 2.7 | N/S | N/S | 290 | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.017 | 0.3 | N/S | <0.02 | 0.019 | <0.2 | <0.005 | 0.021 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 80 | 30 | 325 | T/X | 5
2015-11-18 | 4.29 | 7.3 | 8.8 | 22 | 14 | N/S | 37 | 29 | 758 | 116 | 4 | <0.1 | 10.2 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-19 | 2.85 | 7.4 | 8.3 | 11 | 6 | N/S | 18 | 13 | 784 | 92 | 3 | 0.1 | 10.93 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-20 | 2.61 | 7.5 | 8 | N/S | N/S | N/S | 22 | 14 | 986 | 122 | 2 | 0.1 | 14.97 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-21 | 2.58 | 7.4 | 8.7 | N/S | N/S | N/S | 16 | 11 | 1269 | 144 | 3 | 0.2 | 16.28 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-22 | 2.65 | 7.4 | 8.4 | 10 | 6 | N/S | 14 | 11 | 1281 | 150 | 3 | 0.1 | 14.87 | 3.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-23 | 2.65 | 7.5 | 9.3 | 8 | 5 | <5 | 12 | 6 | 1414 | 248 | 3 | 0.1 | 16.41 | 2.1 | <0.005 | <5 | N/S | 0.7 | 2600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-11-24 | 2.63 | 7.4 | 9.3 | 8 | 3 | N/S | 12 | 7 | 1360 | 168 | 2 | 0.1 | 16.11 | 2 | N/S | N/S | 470 | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 86 | 33 | 351 | 7.7 | 4
2015-11-25 | 3 | 7.4 | 7.5 | 6 | 4 | N/S | 10 | 7 | 1208 | 138 | 2 | 0.1 | 14.64 | 1.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-26 | 4.34 | 7.3 | 6.5 | 7 | 4 | N/S | 10 | 7 | 1054 | 168 | 2 | 0.1 | 9.29 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-27 | 4.43 | 7.3 | 7.6 | N/S | N/S | N/S | 5 | <4 | 768 | 134 | 2 | <0.1 | 7.79 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-28 | 4.45 | 7.3 | 8.3 | N/S | N/S | N/S | <4 | <4 | 832 | 148 | 2 | 0.1 | 9.68 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-29 | 4.41 | 7.3 | 8 | 7 | 3 | N/S | 9 | 6 | 936 | 130 | 2 | 0.2 | 11.42 | 1.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-11-30 | 3.64 | 7.3 | 8.6 | 4 | 2 | <5 | 6 | 4 | 1010 | 162 | 2 | 0.2 | 12.75 | 1.5 | <0.005 | 6 | N/S | 0.6 | 8900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-12-01 | 4.32 | 7.3 | 7.8 | 3 | <2 | N/S | 5 | 4 | 844 | 130 | 1 | 0.1 | 11.23 | 1.1 | N/S | N/S | 253 | N/S | N/S | <0.05 | 0.033 | <0.001 | <0.005 | 0.011 | 0.1 | <0.1 | <0.02 | 0.004 | <0.2 | <0.005 | 0.012 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 78 | 31 | 324 | 3.3 | 4
2015-12-02 | 4.32 | 7.4 | 9 | 5 | 3 | N/S | 10 | 9 | 798 | 80 | 2 | 0.1 | 10.68 | 1.2 | N/S | N/S | 243 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-03 | 4.28 | 7.4 | 9.9 | 7 | 4 | N/S | 10 | 8 | 850 | 94 | 1 | 0.1 | 11.78 | 1.3 | N/S | N/S | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-04 | 3.67 | 7.3 | 9.2 | N/S | N/S | N/S | 8 | 5 | 954 | 144 | 2 | <0.1 | 12.49 | 1.5 | N/S | N/S | 260 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-05 | 2.75 | 7.4 | 9 | N/S | N/S | N/S | 8 | 7 | 1028 | 146 | 2 | 0.1 | 14.97 | 1.8 | N/S | N/S | 286 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-06 | 2.8 | 7.5 | 8.6 | 5 | 3 | N/S | 8 | 7 | 1080 | 174 | 2 | 0.1 | 16.3 | 2.1 | N/S | N/S | 299 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-07 | 3.48 | 7.5 | 7.7 | 6 | 4 | <5 | 16 | 10 | 1060 | 160 | 2 | 0.1 | 14.47 | 1.8 | <0.005 | <5 | 292 | 0.7 | 5100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-12-08 | 3.97 | 7.4 | 7.5 | 7 | 3 | N/S | 16 | 11 | 944 | 134 | 3 | <0.1 | 13.44 | 1.7 | N/S | N/S | 261 | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.011 | 0.2 | N/S | <0.02 | 0.011 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 79 | 32 | 332 | 7.6 | 5
2015-12-09 | 2.86 | 7.5 | 9.8 | 9 | 4 | N/S | 13 | 11 | 1062 | 142 | 3 | 0.1 | 16.34 | 2.2 | N/S | N/S | 305 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-10 | 2.61 | 7.5 | 8.2 | 6 | 3 | N/S | 8 | <4 | 1280 | 252 | 2 | 0.2 | 16.88 | 2.4 | N/S | N/S | 373 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-11 | 2.12 | 7.5 | 9.5 | N/S | N/S | N/S | 8 | 5 | 1151 | 146 | 2 | 0.1 | 17.99 | 2.4 | N/S | N/S | 355 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-12 | 2.28 | 7.5 | 8.1 | N/S | N/S | N/S | 12 | 10 | 1138 | 128 | 3 | 0.2 | 18.8 | 2.7 | N/S | N/S | 330 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-13 | 2.82 | 7.5 | 8.3 | 5 | 3 | N/S | 5 | 4 | 994 | 110 | 2 | 0.5 | 15.86 | 2.2 | N/S | N/S | 306 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-14 | 4.44 | 7.8 | 9.4 | 3 | 2 | <5 | 5 | <4 | 714 | 124 | 1 | <0.1 | 7.85 | 1 | 0.009 | <5 | 175 | 0.4 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-12-15 | 4.38 | 7.7 | 9 | 3 | <2 | N/S | <4 | <4 | 700 | 120 | 1 | 0.2 | 7.76 | 0.8 | N/S | N/S | 172 | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.012 | <0.2 | <0.005 | <0.005 | <0.001 | 0.01 | <0.05 | <0.001 | <0.1 | N/S | 72 | 30 | 302 | 8.5 | 6
2015-12-16 | 3.46 | 7.5 | 8.1 | 13 | 8 | N/S | 27 | 19 | 1036 | 230 | 3 | 0.2 | 8.87 | 1.2 | N/S | N/S | 297 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-17 | 3.89 | 7.6 | 8 | T/X | T/X | N/S | 15 | 10 | 1139 | 184 | 2 | 0.4 | 9.72 | 1.1 | N/S | N/S | 345 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-18 | 4.21 | 7.5 | 8.6 | N/S | N/S | N/S | 30 | 23 | 946 | 210 | 4 | 1.3 | 9.47 | 1.4 | N/S | N/S | 251 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-19 | 3.33 | 7.5 | 9.1 | N/S | N/S | N/S | 28 | 21 | 1116 | 152 | 4 | 1.5 | 10.3 | 1.4 | N/S | N/S | 352 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-20 | 2.55 | 7.5 | 8 | 16 | 8 | N/S | 22 | 16 | 1130 | 150 | 3 | 0.6 | 13.55 | 1.7 | N/S | N/S | 345 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-21 | 4.22 | 7.4 | 8.3 | 15 | 7 | <5 | 35 | 26 | 952 | 140 | 5 | 1.3 | 9.67 | 1.6 | <0.005 | 11 | 303 | 0.6 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-22 | 4.37 | 7.5 | 8.7 | 10 | 6 | N/S | 25 | 18 | 908 | 126 | 3 | 0.2 | 9.19 | 1.1 | N/S | N/S | 269 | N/S | N/S | <0.05 | 0.035 | 0.001 | <0.005 | 0.013 | 0.3 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 74 | 32 | 316 | 12.3 | 6
2015-12-23 | 3.93 | 7.5 | 5.5 | 5 | 3 | N/S | 5 | <4 | 890 | 136 | 2 | 0.2 | 9.23 | 1.1 | N/S | N/S | 268 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-12-24 | 4.31 | 7.4 | 8.9 | T/X | T/X | N/S | 18 | 12 | 742 | 130 | 3 | 0.2 | 8.47 | 1.1 | N/S | N/S | 185 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-25 | 4.23 | 7.4 | 7.4 | N/S | N/S | N/S | <4 | <4 | 846 | 106 | 2 | 1.1 | 11.12 | 1.2 | N/S | N/S | 223 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-26 | 3.47 | 7.5 | 8 | N/S | N/S | N/S | 11 | 9 | 934 | 156 | 3 | 1.8 | 13.4 | 1.6 | N/S | N/S | 247 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-27 | 4.3 | 7.5 | 8.9 | T/X | T/X | N/S | 10 | 7 | 810 | 106 | 2 | 0.4 | 11.54 | 1.3 | N/S | N/S | 217 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-28 | 4.32 | 7.4 | 9.2 | T/X | T/X | <5 | 4 | <4 | 944 | 94 | 1 | 0.2 | 11.16 | 1.1 | <0.005 | <5 | 301 | 0.5 | 20000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2015-12-29 | 4.33 | 7.3 | 9.7 | 3 | <2 | N/S | 5 | <4 | 776 | 110 | 1 | 0.1 | 7.07 | 0.5 | N/S | N/S | 252 | N/S | N/S | <0.05 | 0.029 | <0.001 | <0.005 | 0.007 | 0.1 | N/S | <0.02 | 0.005 | <0.2 | <0.005 | <0.005 | <0.001 | 0.01 | <0.05 | <0.001 | <0.1 | N/S | 68 | 29 | 286 | T/X | 4
2015-12-30 | 4.34 | 7.4 | 9.7 | <2 | <2 | N/S | <4 | <4 | 820 | 116 | 1 | 0.2 | 8.04 | 0.5 | N/S | N/S | 259 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2015-12-31 | 4.31 | 7.4 | 9.8 | <2 | <2 | N/S | <4 | <4 | 1032 | 104 | 1 | 0.1 | 9.86 | 0.6 | N/S | N/S | 317 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
PQL |  |  |  | 2 | 2 | 5 | 4 | 4 | 100 |  | 1 | 0.1 | 0.15 | 0.1 | 0.005 | 5 | 10 | 0.1 |  | 0.05 | 0.004 | 0.001 | 0.005 | 0.005 | 0.1 | 0.1 | 0.02 | 0.001 | 0.2 | 0.005 | 0.005 | 0.001 | 0.01 | 0.05 | 0.001 | 0.1 | 6 | 1 | 1 |  | 0.5 | 1
Observations | 365 | 365 | 365 | 237 | 238 | 52 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 52 | 52 | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 49 | 52
Minimum | 0 | 7.1 | 5 | <2 | <2 | <5 | <4 | <4 | 700 | 74 | 1 | <0.1 | 7.07 | 0.5 | <0.005 | <5 | 155.6 | 0.4 | 990 | <0.05 | 0.027 | <0.001 | <0.005 | <0.005 | 0.1 | <0.1 | <0.02 | 0.004 | <0.2 | <0.005 | <0.005 | <0.001 | 0.01 | <0.05 | <0.001 | <0.1 | <6 | 64 | 28 | 281 | <0.5 | 4
Mean | 2.56 | 7.4 | 8.6 | <9 | <5 | <5 | <11 | <9 | 1271 | 187 | 3 | <0.4 | 17.19 | 2.5 | <0.006 | <6 | 306.4 | 0.8 | 11113 | <0.05 | 0.038 | <0.001 | <0.005 | <0.011 | 0.2 | <0.1 | <0.02 | 0.014 | <0.2 | <0.005 | <0.012 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 91 | 36 | 377 | <2.5 | 5
Maximum | 4.45 | 7.8 | 10 | 26 | 17 | 7 | 48 | 41 | 2197 | 452 | 10 | 3.8 | 26.16 | 12.3 | 0.012 | 11 | 497 | 1.2 | 86000 | <0.05 | 0.057 | 0.002 | <0.005 | 0.02 | 5.9 | 0.1 | <0.02 | 0.049 | <0.2 | <0.005 | 0.04 | 0.001 | 0.05 | <0.05 | <0.001 | <0.1 | 15 | 124 | 45 | 494 | 19.4 | 7
Std Dev | 0.79 | 0.1 | 1.1 | 4 | 2 | 0 | 7 | 5 | 262 | 59 | 1 | 0.5 | 4.1 | 0.9 | 0.002 | 1 | 76.8 | 0.2 | 17262 | 0 | 0.006 | 0 | 0 | 0.004 | 0.8 | 0 | 0 | 0.008 | 0 | 0 | 0.009 | 0 | 0.01 | 0 | 0 | 0 | 1 | 12 | 5 | 49 | 3.7 | 1
January 3, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
February 2, 2015 CN: Aliquot holding time exceeded.
February 15, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
February 16, 2015 F: Sample MS recovery failed, but LCS passed.
February 25, 2015 BOD5, CBOD5, T/X: Batch water blank failure.
March 1, 15, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
March 1, 15, 2015 BOD5, CBOD5, T/X: Batch water blank failure.
March 28, 2015 TKN, P-TOT: Sample MS recovery failed, but LCS passed.
April 6, 26, 2015 BOD5, CBOD5, T/X: Batch LCS failure.
April 8, 16, 25, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
April 9, 14, 2015 BOD5, CBOD5, T/X: Batch water blank failure.
April 25, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
May 7, 13, 2015 BOD5, CBOD5, T/X: Batch LCS failure.
May 13, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
May 25, 2015 Phenol: Aliquot not thermally preserved.
May 27, 2015 TKN: Sample MS recovery failed, but LCS passed.
May 30, 2015 NH3-N: Sample MS recovery failed, but LCS passed.
June 1, 2015 Phenol: Aliquot not thermally preserved.
June 1, 2015 CN: Sample arrived in the lab insufficiently preserved.
June 9, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
June 11, 2015 TKN: Sample MS recovery failed, but LCS passed.
July 8, 22, 25, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
July 14, 2015 Hg: Sample MS recovery failed, but LCS passed.
July 16, 22, 2015 BOD5, CBOD5, T/X: Batch water blank failure.
July 27, 2015 F T/X: Sample never arrived at laboratory.
July 27, 2015 BOD5, CBOD5, T/X: pH not adjusted prior to analysis.
July 30, 2015 BOD5, CBOD5, T/X: Batch LCS failure.
August 1, 11, 20, 2015 NH3-N: Sample MS recovery failed, but LCS passed.
August 1, 11, 20, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
August 16, 31, 2015 BOD5, CBOD5, T/X: Batch LCS failure.
September 3, 4, 10, 18, 23, 2015 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
September 17, 2015 BOD5, CBOD5, T/X: Batch LCS failure.
September 18, 2015 NH3-N: Sample MS recovery failed, but LCS passed.
September 20, 25, 29, 2015 TKN: Sample MS recovery failed, but LCS passed.
September 28, 2015 FOG: Calibration of analytical balance was not verified.
October 1, 14, 2015 TKN: Sample MS recovery failed, but LCS passed.
October 12, 2015 BOD5, CBOD5, T/X: Batch LCS failure
October 14, 2015 TOT PHOS: Sample MS recovery failed, but LCS passed.
October 21 2015 NO2+NO3: Sample MS recovery failed, but LCS passed.
November 4, 2015 BOD5, CBOD5, T/X: Batch LCS failure
November 12 BOD5, CBOD5 T/X: Batch water blank failure.
November 12 BOD5, CBOD5 T/X: Batch water blank failure.
December 8, 13, 2015 NO2+NO3: Sample MS recovery failed, but LCS passed.
December 17, 2015 BOD5, CBOD5 T/X: Batch water blank failure.
December 17, 2015 NH3_N: Sample MS recovery failed, but LCS passed.
December 24, 27, 28, 2015 BOD5, CBOD5 T/X: Batch LCS failure.
December 24, 27, 28, 29 , 2015 TS, TVS: Sample/aliquot holding time exceeded.

## Lemont Outfall 2016
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2016-01-01 | 4.26 | 7.4 | 8.3 | N/S | N/S | N/S | 9 | 8 | 1029 | 138 | 2 | 0.1 | 10.24 | 0.8 | N/S | N/S | 324 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-02 | 4.22 | 7.3 | 9.5 | N/S | N/S | N/S | 12 | 9 | 1015 | 134 | 2 | 0.2 | 10.19 | 0.9 | N/S | N/S | 303 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-03 | 4.17 | 7.4 | 9.6 | T/X | T/X | N/S | 7 | 6 | 960 | 70 | 2 | 0.3 | 10.59 | 1.4 | N/S | N/S | 321 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-04 | 4.02 | 7.4 | 8.3 | T/X | T/X | T/X | 10 | 8 | 958 | 106 | 2 | 0.2 | 10.24 | 1.4 | <0.005 | 8 | 313 | 0.6 | 24000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-01-05 | 4.23 | 7.4 | 9.5 | T/X | T/X | N/S | 8 | 6 | 928 | 86 | 1 | 0.2 | 10.95 | 1.4 | N/S | N/S | 293 | N/S | N/S | <0.05 | 0.034 | <0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.007 | <0.2 | <0.005 | 0.011 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 83 | 35 | 353 | T/X | 5
2016-01-06 | 3.15 | 7.4 | 9.8 | T/X | T/X | N/S | 4 | <4 | 1016 | 114 | 3 | 0.6 | 13.65 | 2.4 | N/S | N/S | 313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-07 | 2.83 | 7.4 | 9.4 | T/X | T/X | N/S | 4 | 4 | 1125 | 122 | 2 | 0.3 | 16.04 | 2.6 | N/S | N/S | 363 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-08 | 3.62 | 7.4 | 9.5 | N/S | N/S | N/S | <4 | <4 | 542 | 80 | 2 | 0.2 | 13.73 | 1.7 | N/S | N/S | 324 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-09 | 4.38 | 7.4 | 9.2 | N/S | N/S | N/S | <4 | <4 | 794 | 102 | 1 | 0.1 | 9.52 | 1.1 | N/S | N/S | 248 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-10 | 3.76 | 7.4 | 9.9 | T/X | T/X | N/S | 4 | 4 | 926 | 132 | 1 | 0.1 | 9.55 | 1.1 | N/S | N/S | 312 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-11 | 3.18 | 7.5 | 10 | T/X | T/X | <5 | 4 | <4 | 1013 | 124 | 1 | 0.2 | 12.13 | 1.2 | <0.005 | <5 | 326 | 0.5 | 8000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-01-12 | 3.39 | 7.5 | 10 | 5 | 3 | N/S | <4 | <4 | 1143 | 142 | 1 | 0.2 | 13.22 | 1.3 | N/S | N/S | 369 | N/S | N/S | <0.05 | 0.037 | 0.001 | <0.005 | 0.006 | 0.1 | N/S | <0.02 | 0.003 | <0.2 | <0.005 | 0.018 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 91 | 38 | 383 | T/X | 4
2016-01-13 | 2.78 | 7.5 | 10 | T/X | T/X | N/S | 5 | 4 | 1276 | 158 | 1 | 0.2 | 14.24 | 1.5 | N/S | N/S | 408 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-14 | 3.25 | 7.4 | 9 | 7 | 3 | N/S | 7 | 4 | 1204 | 130 | 2 | 0.6 | 14.85 | 1.6 | N/S | N/S | 415 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-15 | 3.41 | 7.4 | 8.8 | N/S | N/S | N/S | 6 | 4 | 1346 | 134 | 2 | 0.2 | 13.94 | 1.6 | N/S | N/S | 490 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-16 | 3.47 | 7.5 | 7.2 | N/S | N/S | N/S | 11 | 9 | 1272 | 138 | 2 | 0.3 | 13.3 | 1.5 | N/S | N/S | 462 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-17 | 2.86 | 7.4 | 9.5 | 9 | 7 | N/S | 6 | 5 | 1251 | 142 | 2 | 0.2 | 14.85 | 1.7 | N/S | N/S | 438 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-18 | 2.84 | 7.4 | 10 | T/X | T/X | <5 | 13 | 10 | 1273 | 138 | 2 | 0.2 | 15.13 | 1.9 | <0.005 | 5 | 435 | 0.8 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-19 | 2.85 | 7.4 | 9.3 | 8 | 5 | N/S | <4 | <4 | 1295 | 158 | 2 | 0.3 | 15.49 | 1.8 | N/S | N/S | 428 | N/S | 57000 | <0.05 | 0.046 | 0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.008 | <0.2 | <0.005 | 0.066 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | <6 | 104 | 41 | 428 | T/X | 6
2016-01-20 | 2.37 | 7.4 | 8.8 | T/X | T/X | N/S | 15 | 13 | 1258 | 156 | 4 | 0.3 | 14.13 | 2.3 | N/S | N/S | 412 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-21 | 2.19 | 7.4 | 7.9 | 8 | 4 | N/S | 9 | 6 | 1260 | 136 | 3 | 0.3 | 15.91 | 2.1 | N/S | N/S | 436 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-22 | 2.32 | 7.4 | 10 | N/S | N/S | N/S | 9 | 8 | 1323 | 170 | 3 | 0.4 | 16.82 | 2.2 | N/S | N/S | 449 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-23 | 2.2 | 7.4 | 8.7 | N/S | N/S | N/S | 10 | 9 | 1245 | 160 | 3 | 0.3 | 17.45 | 2.4 | N/S | N/S | 410 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-24 | 2.29 | 7.3 | 9.2 | 9 | 5 | N/S | 12 | 9 | 1224 | 170 | 3 | 0.5 | 16.84 | 2.3 | N/S | N/S | 392 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-25 | 2.29 | 7.4 | 9.6 | 9 | 5 | <5 | 9 | 9 | 1230 | 146 | 3 | 0.4 | 16.18 | 2.2 | 0.006 | 5 | 401 | 1 | 86000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-01-26 | 2.36 | 7.3 | 9.9 | 7 | 5 | N/S | 10 | 7 | 1318 | 124 | 3 | 0.3 | 14.81 | 2 | N/S | N/S | 472 | N/S | N/S | <0.05 | 0.037 | 0.002 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | 0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 97 | 38 | 399 | 5.1 | 5
2016-01-27 | 2.39 | 7.4 | 9.2 | 9 | 6 | N/S | 12 | 9 | 1367 | 192 | 3 | 0.4 | 16.51 | 2 | N/S | N/S | 468 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-28 | 2.37 | 7.5 | 9.9 | 18 | 12 | N/S | 36 | 29 | 1284 | 174 | 6 | 1.1 | 18.54 | 2.6 | N/S | N/S | 414 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-29 | 2.47 | 7.5 | 9 | N/S | N/S | N/S | 22 | 19 | 1237 | 140 | 5 | 0.9 | 17.56 | 2.4 | N/S | N/S | 409 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-30 | 2.54 | 7.4 | 9.5 | N/S | N/S | N/S | 18 | 16 | 1288 | 152 | 6 | 2.4 | 15.69 | 2.5 | N/S | N/S | 431 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-01-31 | 2.47 | 7.4 | 7.7 | 9 | 6 | N/S | 9 | 6 | 1371 | 172 | 4 | 1.2 | 16.22 | 2.2 | N/S | N/S | 467 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-01 | 2.45 | 7.4 | 9.2 | 6 | 4 | <5 | 5 | 5 | 1442 | 180 | 3 | 0.5 | 17.02 | 2.2 | <0.005 | <5 | 509 | 0.9 | 34000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-02-02 | 3.17 | 7.4 | 6 | 10 | 6 | N/S | 10 | 8 | 1247 | 156 | 3 | 0.4 | 14.13 | 2 | N/S | N/S | 498 | N/S | N/S | <0.05 | 0.037 | <0.001 | <0.005 | 0.013 | 0.2 | <0.1 | <0.02 | 0.017 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 91 | 37 | 379 | 88.2 | 4
2016-02-03 | 4.21 | 7.2 | 7 | 6 | 4 | N/S | 4 | <4 | 994 | 120 | 2 | 0.2 | 8.6 | 1 | N/S | N/S | 368 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-04 | 2.52 | 7.5 | 7.2 | 5 | 3 | N/S | 7 | <4 | 1117 | 160 | 2 | 0.3 | 10.19 | 1.1 | N/S | N/S | 389 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-05 | 2.81 | 7.5 | 6.7 | N/S | N/S | N/S | <4 | <4 | 1109 | 136 | 2 | 0.8 | 12.79 | 1.4 | N/S | N/S | 372 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-06 | 2.52 | 7.4 | 6.6 | N/S | N/S | N/S | <4 | <4 | 1168 | 148 | 2 | 0.4 | 14.24 | 1.7 | N/S | N/S | 378 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-07 | 2.83 | 7.4 | 6.7 | 15 | 11 | N/S | 25 | 18 | 1190 | 190 | 5 | 1 | 16.18 | 2.3 | N/S | N/S | 371 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-08 | 2.46 | 7.4 | 6.1 | 17 | 7 | <5 | 26 | 19 | 1216 | 192 | 4 | 0.6 | 16.98 | 2.3 | <0.005 | <5 | 380 | 0.8 | 3200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-02-09 | 3.31 | 7.5 | 7 | 4 | 3 | N/S | 4 | <4 | 1184 | 200 | 2 | 0.6 | 15.07 | 1.7 | N/S | N/S | 394 | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.011 | 0.1 | N/S | <0.02 | 0.006 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 101 | 40 | 418 | 4.6 | 5
2016-02-10 | 2.85 | 7.4 | 6.8 | 18 | 11 | N/S | 28 | 23 | 1082 | 158 | 5 | 0.8 | 13.32 | 2.2 | N/S | N/S | 382 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-11 | 2.42 | 7.4 | 6.8 | 14 | 8 | N/S | 22 | 18 | 1284 | 156 | 4 | 0.2 | 17.5 | 2.3 | N/S | N/S | 397 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-12 | 2.42 | 7.5 | 7.8 | N/S | N/S | N/S | 23 | 17 | 1487 | 236 | 3 | 0.2 | 17.37 | 2.5 | N/S | N/S | 491 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-13 | 2.42 | 7.4 | 7.4 | N/S | N/S | N/S | 25 | 20 | 1560 | 220 | 4 | 0.2 | 18.11 | 2.6 | N/S | N/S | 534.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-14 | 2.41 | 7.4 | 6.7 | 24 | 12 | N/S | 27 | 23 | 1443 | 190 | 5 | 0.6 | 17.84 | 2.7 | N/S | N/S | 491.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-15 | 2.35 | 7.4 | 6.5 | 23 | 9 | <5 | 22 | 18 | 1450 | 198 | 6 | 0.7 | 17.94 | 2.7 | <0.005 | 6 | 481.7 | 1 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-16 | 2.32 | 7.4 | 6.2 | 19 | 9 | N/S | 7 | 6 | 1708 | 216 | 4 | 1.2 | 16.91 | 2.5 | N/S | N/S | 708 | N/S | 310000 | <0.05 | 0.048 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.043 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | <6 | 118 | 45 | 483 | 5.1 | 7
2016-02-17 | 1.94 | 7.4 | 6 | 14 | 9 | N/S | 9 | 8 | 1646 | 200 | 4 | 0.8 | 16.16 | 2.2 | N/S | N/S | 677 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-18 | 2.07 | 7.3 | 5.8 | 8 | 6 | N/S | 4 | 4 | 1750 | 206 | 3 | 0.8 | 17.71 | 2.1 | N/S | N/S | 751 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-19 | 2.2 | 7.3 | 5.5 | N/S | N/S | N/S | <4 | <4 | 1680 | 160 | 3 | 1 | 17.14 | 2.1 | N/S | N/S | 711 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-20 | 2.25 | 7.3 | 6.9 | N/S | N/S | N/S | 5 | 4 | 1852 | 202 | 3 | 1 | 17.16 | 2.1 | N/S | N/S | 824 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-21 | 2.27 | 7.3 | 6.5 | 9 | 6 | N/S | 7 | 4 | 1758 | 198 | 4 | 1.3 | 16.57 | 2.1 | N/S | N/S | 773 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-22 | 2.14 | 7.3 | 5.4 | 15 | 8 | <5 | 11 | 9 | 1520 | 142 | 5 | 1.6 | 17.1 | 2.3 | <0.005 | 11 | 586 | 1 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-02-23 | 2.07 | 7.4 | 6.2 | 11 | 7 | N/S | 12 | 9 | 1480 | 164 | 5 | 1 | 18.14 | 2.4 | N/S | N/S | 580 | N/S | N/S | <0.05 | 0.042 | 0.001 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.02 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 100 | 40 | 414 | 5.6 | 7
2016-02-24 | 2.04 | 7.4 | 6.5 | 15 | 9 | N/S | 10 | 8 | 1434 | 150 | 4 | 1 | 19.29 | 2.6 | N/S | N/S | 572 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-25 | 2.13 | 7.3 | 6.1 | 13 | 8 | N/S | 14 | 11 | 1618 | 216 | 4 | 0.8 | 19.43 | 2.6 | N/S | N/S | 700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-26 | 2.11 | 7.3 | 7 | N/S | N/S | N/S | 19 | 14 | 1612 | 198 | 5 | 1.1 | 18.99 | 2.7 | N/S | N/S | 683 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-27 | 2.05 | 7.5 | 6.5 | N/S | N/S | N/S | 21 | 16 | 1558 | 198 | 6 | 1.6 | 19.87 | 3 | N/S | N/S | 643 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-28 | 2.29 | 7.4 | 7 | 26 | 12 | N/S | 24 | 19 | 1398 | 130 | 7 | 3.1 | 17.43 | 3 | N/S | N/S | 469 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-02-29 | 2.16 | 7.3 | 6.1 | 24 | 9 | <5 | 20 | 19 | 1294 | 160 | 7 | 3.5 | 15.83 | 3 | <0.005 | 8 | 428 | 1 | 17000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-03-01 | 1.99 | 7.3 | 7.1 | 13 | 9 | N/S | 17 | 12 | 1380 | 156 | 5 | 1.9 | 17.86 | 2.8 | N/S | N/S | 456 | N/S | N/S | <0.05 | 0.04 | <0.001 | <0.005 | 0.016 | 0.2 | 0.1 | <0.02 | 0.022 | <0.2 | <0.005 | 0.022 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 95 | 37 | 392 | 250.2 | 7
2016-03-02 | 1.98 | 7.3 | 6.8 | 16 | 8 | N/S | 17 | 13 | 1341 | 138 | 4 | 1 | 18.49 | 2.6 | N/S | N/S | 456 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-03 | 2.02 | 7.3 | 6.9 | 12 | 6 | N/S | 13 | 9 | 1529 | 186 | 4 | 0.9 | 18.1 | 2.5 | N/S | N/S | 549 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-04 | 2.11 | 7.4 | 5.8 | N/S | N/S | N/S | 15 | 12 | 1756 | 268 | 3 | 0.7 | 17.79 | 2.5 | N/S | N/S | 651 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-05 | 2.14 | 7.4 | 7 | N/S | N/S | N/S | 13 | 10 | 1641 | 232 | 3 | 1 | 16.78 | 2.5 | N/S | N/S | 608 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-06 | 2.17 | 7.3 | 7.5 | 11 | 6 | N/S | 13 | 8 | 1589 | 240 | 4 | 1.5 | 16.43 | 2.5 | N/S | N/S | 575 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-07 | 2.27 | 7.5 | 6.5 | 17 | 8 | <5 | 11 | 10 | 1538 | 216 | 5 | 2.3 | 16.28 | 2.5 | 0.006 | 10 | 540 | 1 | 8600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-03-08 | 2.01 | 7.4 | 5.4 | 16 | 6 | N/S | 13 | 11 | 1450 | 212 | 4 | 1.5 | 16.43 | 2.5 | N/S | N/S | 510 | N/S | N/S | <0.05 | 0.047 | <0.001 | <0.005 | 0.014 | 0.2 | N/S | <0.02 | 0.026 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 100 | 40 | 414 | T/X | 7
2016-03-09 | 2.14 | 7.3 | 6.2 | 17 | 7 | N/S | 15 | 7 | 1484 | 212 | 4 | 1.1 | 17.59 | 2.4 | N/S | N/S | 533 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-10 | 2.12 | 7.5 | 7.9 | 15 | 7 | N/S | 15 | 8 | 1550 | 196 | 5 | 1.1 | 17.96 | 2.4 | N/S | N/S | 551 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-11 | 2.08 | 7.4 | 6.1 | N/S | N/S | N/S | 14 | 11 | 1482 | 212 | 4 | 1 | 18.36 | 2.5 | N/S | N/S | 524 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-12 | 2.13 | 7.4 | 6.1 | N/S | N/S | N/S | 13 | 10 | 1424 | 182 | 4 | 1.2 | 19.02 | 2.7 | N/S | N/S | 486 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-13 | 3.09 | 7.5 | 6 | 17 | 7 | N/S | 18 | 14 | 1264 | 142 | 4 | 1.2 | 13.93 | 2.2 | N/S | N/S | 448 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-14 | 4.6 | 7.3 | 5.2 | 15 | 7 | <5 | 18 | 11 | 1170 | 154 | 3 | 0.8 | 9.55 | 1.2 | 0.007 | <5 | 435 | 0.5 | 66000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-03-15 | 3.64 | 7.5 | 5.7 | 9 | 6 | N/S | 17 | 11 | 1295 | 186 | 2 | 0.2 | 9.51 | 1.1 | N/S | N/S | 471 | N/S | N/S | <0.05 | 0.047 | <0.001 | <0.005 | 0.013 | 0.2 | N/S | <0.02 | 0.017 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 96 | 41 | 409 | 10 | 4
2016-03-16 | 3.65 | 7.4 | 7.4 | 9 | 5 | N/S | 16 | 11 | 1251 | 174 | 2 | 0.2 | 10.83 | 1.2 | N/S | N/S | 461 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-17 | 2.81 | 7.3 | 7.4 | 10 | 6 | N/S | 11 | 7 | 1247 | 158 | 3 | 0.4 | 11.87 | 1.2 | N/S | N/S | 466 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-18 | 2.59 | 7.5 | 6.8 | N/S | N/S | N/S | 14 | 9 | 1355 | 196 | 3 | 0.3 | 12.62 | 1.5 | N/S | N/S | 478 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-19 | 3.1 | 7.4 | 7.3 | N/S | N/S | N/S | 13 | 11 | 1266 | 160 | 3 | 1.2 | 12.78 | 1.6 | N/S | N/S | 429 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-20 | 3.36 | 7.6 | 6.5 | 24 | 8 | N/S | 15 | 12 | 1164 | 182 | 5 | 2.7 | 11.41 | 1.7 | N/S | N/S | 394 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-21 | 3.02 | 7.3 | 7.6 | 15 | 5 | <5 | 7 | 4 | 1148 | 114 | 5 | 2.3 | 11.82 | 1.7 | 0.005 | 5 | 365 | 0.7 | 28000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-03-22 | 3.61 | 7.4 | 6.8 | 22 | 7 | N/S | 19 | 14 | 1157 | 140 | 5 | 2.5 | 11.64 | 1.8 | N/S | N/S | 361 | N/S | N/S | <0.05 | 0.041 | <0.001 | <0.005 | 0.015 | 0.2 | N/S | <0.02 | 0.029 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 84 | 37 | 362 | 3.9 | 5
2016-03-23 | 2.49 | 7.4 | 6.5 | 18 | 7 | N/S | 18 | 13 | 1141 | 160 | 4 | 1.2 | 15.12 | 2.1 | N/S | N/S | 341 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-24 | 4.14 | 7.5 | 5.9 | 26 | 8 | N/S | 28 | 19 | 998 | 150 | 5 | 1.3 | 12.37 | 2 | N/S | N/S | 313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-25 | 4.8 | 7.3 | 7.1 | N/S | N/S | N/S | 26 | 19 | 858 | 122 | 3 | 0.1 | 9.05 | 1.3 | N/S | N/S | 272 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-26 | 2.75 | 7.4 | 6 | N/S | N/S | N/S | 16 | 12 | 984 | 144 | 2 | 0.1 | 10.83 | 1.4 | N/S | N/S | 313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-27 | 3.74 | 7.5 | 6.9 | 18 | 8 | N/S | 23 | 16 | 1054 | 144 | 6 | 2.8 | 10.28 | 1.8 | N/S | N/S | 320 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-03-28 | 3.53 | 7.2 | 6.5 | 17 | 12 | <5 | 21 | 16 | 1138 | 108 | 7 | 3.8 | 7.39 | 2 | 0.011 | 5 | 375 | 0.6 | 27000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-03-29 | 3.41 | 7.2 | 6.8 | 12 | 6 | N/S | 19 | 16 | 1204 | 180 | 4 | 1.2 | 9.85 | 1.5 | N/S | N/S | 370 | N/S | N/S | <0.05 | 0.045 | 0.001 | <0.005 | 0.015 | 0.2 | N/S | <0.02 | 0.019 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 100 | 42 | 425 | N/S | 5
2016-03-30 | 3.82 | 7.4 | 5.5 | 9 | 4 | S/X | 8 | 7 | 1094 | 120 | 3 | 1.5 | 9.99 | 1.3 | N/S | N/S | 339 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 3.7 | N/S
2016-03-31 | 3.69 | 7.3 | 5.2 | 6 | 3 | N/S | <4 | <4 | 1072 | 142 | 3 | 1.7 | 10.11 | 1.3 | N/S | N/S | 333 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-01 | 3.2 | 7.4 | 5.6 | N/S | N/S | N/S | <4 | <4 | 1067 | 124 | 3 | 1.3 | 11.53 | 1.4 | N/S | N/S | 347 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-02 | 3.34 | 7.4 | 6.8 | N/S | N/S | N/S | <4 | <4 | 1104 | 150 | 3 | 1.6 | 11.98 | 1.4 | N/S | N/S | 361 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-03 | 2.58 | 7.4 | 7.1 | 3 | 2 | N/S | <4 | <4 | 1099 | 140 | 3 | 0.5 | 14.06 | 1.4 | N/S | N/S | 353 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-04 | 2.63 | 7.4 | 6.6 | 3 | 3 | <5 | <4 | <4 | 1180 | 114 | 2 | 0.5 | 15.85 | 1.5 | <0.005 | <5 | 382 | 0.7 | 3000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-04-05 | 2.68 | 7.4 | 7.2 | 2 | <2 | N/S | <4 | <4 | 1203 | 144 | 2 | 0.7 | 15.55 | 1.7 | N/S | N/S | 373 | N/S | N/S | <0.05 | 0.044 | 0.002 | <0.005 | 0.008 | 0.1 | <0.1 | <0.02 | 0.005 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 98 | 42 | 417 | 4.7 | 5
2016-04-06 | 2.96 | 7.5 | 6.8 | 2 | <2 | N/S | <4 | <4 | 1148 | 164 | 3 | 1.5 | 13.99 | 1.6 | N/S | N/S | 357 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-07 | 3.15 | 7.3 | 5.9 | 14 | 6 | N/S | 16 | 12 | 1067 | 118 | 3 | 0.6 | 11.6 | 1.4 | N/S | N/S | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-08 | 3.22 | 7.2 | 7.3 | N/S | N/S | N/S | 15 | 10 | 1070 | 128 | 3 | 0.6 | 12.43 | 1.4 | N/S | N/S | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-09 | 3.17 | 7.4 | 6.6 | N/S | N/S | N/S | 22 | 15 | 1072 | 146 | 4 | 1 | 12.99 | 1.7 | N/S | N/S | 343 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-10 | 2.72 | 7.4 | 6.1 | 19 | 9 | N/S | 20 | 17 | 1076 | 176 | 4 | 1.7 | 13.83 | 1.9 | N/S | N/S | 335 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-11 | 2.87 | 7.4 | 6.9 | 26 | 5 | <5 | 23 | 18 | 1153 | 128 | 5 | 2.4 | 13.9 | 1.8 | 0.006 | 5 | 376 | 0.7 | 41000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-04-12 | 2.61 | 7.4 | 6.2 | 21 | 7 | N/S | 19 | 12 | 1130 | 106 | 4 | 1.1 | T/X | 1.9 | N/S | N/S | 358 | N/S | N/S | <0.05 | 0.039 | 0.002 | <0.005 | 0.015 | 0.2 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 93 | 40 | 399 | 5.6 | 5
2016-04-13 | 2.51 | 7.3 | 6.5 | T/X | T/X | N/S | 18 | 14 | 1136 | 156 | 4 | 1 | 16.43 | 2.2 | N/S | N/S | 336 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-14 | 2.5 | 7.3 | 5.1 | 6 | 4 | N/S | <4 | <4 | 1158 | 196 | 3 | 1.1 | 16.61 | 2.1 | N/S | N/S | 337 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-15 | 2.5 | 7.3 | 5.7 | N/S | N/S | N/S | <4 | <4 | 1269 | 238 | 4 | 2.1 | 17.68 | 2.3 | N/S | N/S | 370 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-16 | 2.47 | 7.4 | 6.1 | N/S | N/S | N/S | <4 | <4 | 1281 | 230 | 5 | 3.2 | 15.93 | 2.4 | N/S | N/S | 376 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-17 | 2.28 | 7.4 | 6.3 | 9 | 7 | N/S | <4 | <4 | 1228 | 210 | 6 | 4.9 | 14.37 | 2.4 | N/S | N/S | 363 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-18 | 2.29 | 7.5 | 5.9 | 9 | 7 | <5 | 4 | <4 | 1273 | 174 | 9 | 7.4 | 11.57 | 2.3 | <0.005 | 5 | <10 | 1 | 150000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-04-19 | 2.03 | 7.5 | 5.2 | 13 | 8 | N/S | 5 | 5 | 1242 | 174 | 9 | 6.4 | 12.88 | 2.4 | N/S | N/S | 362 | N/S | N/S | <0.05 | 0.042 | 0.016 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.02 | <0.2 | <0.005 | <0.005 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 100 | 41 | 422 | 4.3 | 7
2016-04-20 | 2.06 | 7.4 | 5.4 | 13 | 7 | N/S | 7 | 6 | 1216 | 170 | 9 | 6.6 | 11.87 | 2.5 | N/S | N/S | 371 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-21 | 2.31 | 7.3 | 5.1 | 9 | 5 | N/S | 28 | 6 | 1002 | 138 | 4 | 2.9 | 14.43 | 2.3 | N/S | N/S | 269 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-22 | 2.37 | 7.3 | 4.8 | N/S | N/S | N/S | 27 | 20 | 1288 | 228 | 7 | 2.3 | 15.75 | 2.7 | N/S | N/S | 395 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-23 | 2.37 | 7.4 | 6.4 | N/S | N/S | N/S | 34 | 26 | 1620 | 262 | 9 | 4.7 | 14.27 | 2.9 | N/S | N/S | 550 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-24 | 2.34 | 7.5 | 6.6 | 17 | 10 | N/S | 17 | 14 | 1502 | 200 | 7 | 3.7 | 15.21 | 2.7 | N/S | N/S | 508 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-25 | 2.28 | 7.4 | 5.1 | 18 | 14 | <5 | 28 | 25 | 1576 | 216 | 7 | 2.7 | 15.66 | 2.9 | 0.005 | <5 | 530 | 0.9 | 30000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-04-26 | 2.18 | 7.1 | 4.5 | T/X | 20 | N/S | 40 | 34 | 1454 | 124 | 16 | 11.5 | 10.61 | 2.8 | N/S | N/S | 501 | N/S | N/S | <0.05 | 0.045 | 0.007 | <0.005 | 0.023 | 0.3 | N/S | <0.02 | 0.038 | <0.2 | <0.005 | <0.005 | <0.001 | 0.06 | <0.05 | <0.001 | <0.1 | N/S | 101 | 42 | 425 | T/X | 8
2016-04-27 | 2.65 | 7.4 | 4.6 | 17 | 13 | N/S | 10 | 6 | 1282 | 102 | 17 | 13.7 | 7.11 | 2.5 | N/S | N/S | 456 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-28 | 3.62 | 7.5 | 5.4 | 12 | 6 | N/S | 7 | 4 | 1232 | 144 | 13 | 11 | 5.2 | 1.9 | N/S | N/S | 419 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-29 | 2.47 | 7.4 | 5.6 | N/S | N/S | N/S | <4 | <4 | 1220 | 134 | 11 | 8.8 | 8.12 | 2.2 | N/S | N/S | 412 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-04-30 | 3.15 | 7.4 | 5.6 | N/S | N/S | N/S | <4 | <4 | 1073 | 106 | 10 | 8.1 | 7.45 | 2 | N/S | N/S | 355 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-01 | 4.39 | 7.4 | 5.1 | 5 | 5 | N/S | <4 | <4 | 942 | 92 | 9 | 7 | 5.1 | 1.49 | N/S | N/S | 288 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-02 | 4.41 | 7.3 | 5.7 | 7 | 5 | <5 | <4 | <4 | 904 | 104 | 7 | 5.5 | 5.6 | 1.27 | 0.005 | 8 | 268 | 0.6 | 41000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-05-03 | 3.98 | 7.4 | 5.8 | 7 | 5 | N/S | <4 | <4 | 924 | 92 | 8 | 6.6 | 5.78 | 1.5 | N/S | N/S | 272 | N/S | N/S | <0.05 | 0.035 | 0.001 | <0.005 | 0.009 | 0.1 | <0.1 | <0.02 | 0.02 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 83 | 36 | 355 | 7.9 | 6
2016-05-04 | 3.62 | 7.4 | 5.7 | 6 | 5 | N/S | <4 | <4 | 912 | 118 | 9 | 6.5 | 7.67 | 1.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-05 | 3.03 | 7.4 | 5.7 | 6 | 5 | N/S | <4 | <4 | 1010 | 142 | 8 | 5.7 | 9.24 | 1.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-06 | 2.58 | 7.4 | 4.9 | N/S | N/S | N/S | 26 | 20 | 1112 | 146 | 11 | 7.2 | 9.8 | 2.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-07 | 3.02 | 7.4 | 6.3 | N/S | N/S | N/S | 21 | 16 | 1176 | 166 | 13 | 10.4 | 8.86 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-08 | 2.42 | 7.6 | 7.4 | 15 | 7 | N/S | 8 | 7 | 1120 | 146 | 14 | 11.4 | 8.59 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-09 | 2.67 | 7.5 | 6.8 | 29 | 9 | <5 | 10 | 8 | 1150 | 154 | 14 | 10.6 | 10.98 | 3.08 | 0.011 | 5 | N/S | 0.9 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-05-10 | 4.48 | 7.4 | 5.2 | 6 | 4 | N/S | 18 | 16 | 846 | 120 | 7 | 5.8 | 7.83 | 1.68 | N/S | N/S | 239 | N/S | N/S | <0.05 | 0.031 | <0.001 | <0.005 | 0.009 | 0.1 | N/S | <0.02 | 0.014 | <0.2 | <0.005 | <0.005 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 75 | 32 | 320 | 6.8 | 7
2016-05-11 | 4.57 | 7.2 | 5.2 | 4 | 3 | N/S | <4 | <4 | 770 | 122 | 3 | 1 | 8.71 | 1.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-12 | 4.19 | 7.3 | 5.3 | 15 | 6 | N/S | 17 | 15 | 882 | 130 | 5 | 2.6 | 8.55 | 1.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-13 | 3.14 | 7.4 | 5.4 | N/S | N/S | N/S | <4 | <4 | 906 | 136 | 3 | 1.6 | 10.85 | 1.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-14 | 4.41 | 7.3 | 5.2 | N/S | N/S | N/S | <4 | 4 | 846 | 114 | 4 | 1.9 | 9.02 | 1.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-15 | 4.06 | 7.3 | 5.1 | 3 | <2 | N/S | 16 | 12 | 838 | 116 | 3 | 2.4 | 8.6 | 1.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-16 | 4.2 | 7.3 | 5.1 | 4 | 3 | <5 | <4 | <4 | 844 | 94 | 5 | 4.1 | 7.52 | 1.37 | 0.005 | <5 | N/S | 0.7 | 5300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-05-17 | 3.64 | 7.3 | 5.1 | T/X | T/X | N/S | <4 | <4 | 952 | 100 | 6 | 5.3 | 8.04 | 1.45 | N/S | N/S | 256 | N/S | N/S | <0.05 | 0.038 | <0.001 | <0.005 | 0.008 | 0.1 | N/S | <0.02 | 0.015 | <0.2 | <0.005 | 0.019 | <0.001 | 0.02 | <0.05 | <0.001 | <0.1 | N/S | 93 | 40 | 398 | 6.4 | 5
2016-05-18 | 3.53 | 7.3 | 5.6 | 4 | 3 | N/S | <4 | <4 | 1046 | 132 | 7 | 4.9 | 8.87 | 1.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-19 | 2.72 | 7.4 | 5 | T/X | T/X | N/S | 4 | <4 | 1118 | 136 | 8 | 4.9 | 11.37 | 1.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-20 | 2.5 | 7.3 | 5.5 | N/S | N/S | N/S | 14 | 8 | 1213 | 242 | 5 | 3.3 | 15.37 | 2.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-21 | 2.81 | 7.2 | 6.4 | N/S | N/S | N/S | 12 | 8 | 1328 | 266 | 7 | 4.9 | 14.26 | 2.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-22 | 2.5 | 7.3 | 5.2 | 13 | 6 | N/S | 10 | 7 | 1323 | 230 | 9 | 7.3 | 10.48 | 2.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-23 | 2.46 | 7.3 | 5 | T/X | T/X | <5 | 10 | 6 | 1408 | 254 | 8 | 5.5 | 12.85 | 2.64 | 0.005 | 7 | N/S | 1 | 9500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-05-24 | 2.49 | 7.4 | 4.7 | T/X | T/X | N/S | 5 | <4 | 1424 | 234 | 6 | 4.1 | 14.32 | 2.59 | N/S | N/S | 442 | N/S | N/S | <0.05 | 0.048 | <0.001 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.022 | <0.2 | <0.005 | 0.034 | 0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 120 | 44 | 484 | 4.5 | 5
2016-05-25 | 2.63 | 7.3 | 5.4 | 14 | 6 | N/S | 13 | 10 | 1408 | 252 | 6 | 3.4 | 13.94 | 2.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-26 | 2.69 | 7.4 | 4.2 | 13 | 5 | N/S | 12 | 8 | 1289 | 226 | 5 | 2.1 | 14.56 | 2.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-27 | 2.79 | 7.2 | 4.4 | N/S | N/S | N/S | <4 | 4 | 1318 | 246 | 5 | 2.1 | 15.57 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-28 | 2.39 | 7.3 | 4.1 | N/S | N/S | N/S | 4 | 4 | 1270 | 238 | 4 | 1.5 | 15.26 | 2.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-29 | 2.42 | 7.4 | 4.8 | 7 | 4 | N/S | 4 | <4 | 1224 | 212 | 4 | 1 | 16.47 | 2.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-30 | 2.42 | 7.3 | 3.9 | 9 | 5 | <5 | 4 | <4 | 1255 | 206 | 4 | 1.4 | 16.12 | 2.69 | <0.005 | 5 | N/S | 0.9 | N/R | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-05-31 | 2.96 | 7.4 | 3.7 | 18 | 7 | N/S | 10 | 9 | 1188 | 208 | 4 | 1.7 | 12.75 | 2.45 | N/S | N/S | 369 | N/S | 18000 | <0.05 | 0.048 | <0.001 | <0.005 | 0.015 | 0.1 | N/S | <0.02 | 0.03 | <0.2 | <0.005 | 0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | <6 | 100 | 38 | 404 | 6.1 | 6
2016-06-01 | 4.1 | 7.2 | 3.6 | T/X | T/X | N/S | 14 | 12 | 938 | 148 | 4 | 0.9 | 9.84 | 1.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-02 | 2.64 | 7.3 | 4.4 | 11 | 4 | N/S | <4 | <4 | 590 | 124 | 2 | 0.6 | 10.76 | 1.46 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-03 | 2.74 | 7.3 | 4.4 | N/S | N/S | N/S | 16 | 14 | 1048 | 154 | 3 | 0.4 | 14.55 | 2.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-04 | 2.46 | 7.3 | 5.9 | N/S | N/S | N/S | 19 | 13 | 1146 | 186 | 4 | 0.5 | 16.13 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-05 | 2.45 | 7.4 | 5.2 | T/X | T/X | N/S | 12 | 10 | 1082 | 156 | 4 | 1.3 | 16.13 | 2.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-06 | 2.44 | 7.3 | 4.7 | 14 | 8 | <5 | 8 | 8 | 1167 | 246 | 4 | 1.9 | 15.66 | 2.54 | 0.005 | <5 | N/S | 1 | 17000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 8 | N/S | N/S | N/S | N/S | N/S
2016-06-07 | 2.44 | 7.2 | 5.3 | 25 | 9 | N/S | 19 | 15 | 1194 | 198 | 5 | 1.6 | 15.59 | 2.76 | N/S | N/S | 334.8 | N/S | N/S | <0.05 | 0.046 | <0.001 | <0.005 | 0.023 | 0.2 | 0.1 | <0.02 | 0.035 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 106 | 40 | 431 | 8.1 | 8
2016-06-08 | 2.42 | 7.3 | 4.5 | T/X | T/X | N/S | 8 | 7 | 1116 | 164 | 6 | 1.9 | 15.55 | 3.01 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-09 | 2.39 | 7.4 | 6.8 | 25 | 11 | N/S | 16 | 14 | 1182 | 220 | 5 | 1.9 | 12.84 | 3.07 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-10 | 2.39 | 7.5 | 5.8 | N/S | N/S | N/S | 8 | 5 | 1052 | 134 | 5 | 1.9 | 11.01 | 3.02 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-11 | 2.37 | 7.4 | 5 | N/S | N/S | N/S | 4 | 4 | 1026 | 126 | 6 | 3.3 | 7.98 | 3.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-12 | 2.27 | 7.4 | 4.9 | 22 | 9 | N/S | 8 | 6 | 1116 | 108 | 7 | 4.7 | 5.64 | 3.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-13 | 2.38 | 7.4 | 4.4 | 11 | 9 | <5 | 8 | 6 | 1282 | 188 | 8 | 6.2 | 6.03 | 3.23 | T/X | 5 | N/S | 1 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-06-14 | 2.32 | 7.5 | 5 | 14 | 9 | N/S | 6 | 7 | 1130 | 188 | 11 | 8.5 | 6.59 | 2.85 | N/S | N/S | 316 | N/S | N/S | <0.05 | 0.042 | <0.001 | <0.005 | 0.012 | 0.1 | N/S | <0.02 | 0.028 | <0.2 | <0.005 | <0.005 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 99 | 39 | 409 | 4.6 | 7
2016-06-15 | 3.09 | 7.4 | 4.9 | 20 | 11 | N/S | 26 | 23 | 880 | 158 | 9 | 6 | 7.57 | 2.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-16 | 2.28 | 7.4 | 4.6 | 12 | 6 | N/S | 14 | 12 | 928 | 148 | 6 | 2.5 | 14.08 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-17 | 2.41 | 7.2 | 3.9 | N/S | N/S | N/S | 18 | 13 | 906 | 160 | 6 | 2.7 | 15.63 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-18 | 2.47 | 7.4 | 5.5 | N/S | N/S | N/S | 24 | 18 | 1075 | 208 | 6 | 2.8 | 17.34 | 3.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-19 | 2.44 | 7.6 | 4.8 | 18 | 10 | N/S | 25 | 19 | 1300 | 270 | 6 | 2.5 | 17.39 | 3.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-20 | 2.43 | 7.1 | 4.5 | 17 | 8 | <5 | 16 | 12 | 1414 | 258 | 5 | 3.3 | 17.38 | 3.51 | 0.006 | <5 | N/S | 0.9 | 6400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 15 | N/S | N/S | N/S | N/S | N/S
2016-06-21 | 2.39 | 7.4 | 5.5 | 16 | 8 | N/S | 14 | 11 | 1438 | 296 | 4 | 2.4 | 18.01 | 3.52 | N/S | N/S | 428 | N/S | N/S | <0.05 | 0.047 | 0.006 | <0.005 | 0.014 | 0.1 | N/S | <0.02 | 0.021 | <0.2 | <0.005 | 0.01 | <0.001 | 0.04 | <0.05 | <0.001 | <0.1 | N/S | 108 | 39 | 432 | 4 | 5
2016-06-22 | 2.32 | 7.3 | 5.1 | T/X | T/X | N/S | 11 | 9 | 1547 | 356 | 6 | 3.1 | 13.31 | 3.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-23 | 2.3 | 7.4 | 4.4 | 10 | 8 | N/S | 7 | 6 | 1416 | 284 | 4 | 1.2 | 15.87 | 3.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-24 | 2.37 | 7.3 | 5.3 | N/S | N/S | N/S | 6 | 5 | 1238 | 178 | 4 | 1 | 17.68 | 3.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-25 | 2.41 | 7.3 | 4.6 | N/S | N/S | N/S | 8 | 7 | 1396 | 230 | 4 | 1.5 | 17.24 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-26 | 2.99 | 7.4 | 4.7 | 14 | 7 | N/S | 8 | 5 | 1395 | 220 | 6 | 3.5 | 13.48 | 2.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-27 | 2.24 | 7.4 | 4.9 | 12 | 5 | <5 | 5 | <4 | 1334 | 268 | 4 | 1.8 | 15.46 | 2.71 | 0.006 | <5 | N/S | 1 | 22000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-06-28 | 2.36 | 7.4 | 4.3 | 7 | 4 | N/S | 4 | <4 | 1331 | 240 | 3 | 0.6 | 18.82 | 2.86 | N/S | N/S | 417 | N/S | N/S | <0.05 | 0.045 | 0.01 | <0.005 | 0.01 | 0.1 | N/S | <0.02 | 0.009 | <0.2 | <0.005 | 0.014 | <0.001 | 0.03 | <0.05 | <0.001 | <0.1 | N/S | 105 | 39 | 422 | 3.3 | 5
2016-06-29 | 2.39 | 7.3 | 5.4 | 9 | 4 | N/S | 8 | 8 | 1560 | 350 | 3 | 0.6 | 20.83 | 3.09 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-06-30 | 2.36 | 7.3 | 5 | 10 | 5 | N/S | 10 | 6 | 1518 | 346 | 3 | 0.5 | 20.47 | 3.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-01 | 2.34 | 7.3 | 6.5 | N/S | N/S | N/S | 4 | 6 | 1536 | 328 | 3 | 0.5 | 20.85 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-02 | 2.27 | 7.4 | 5.1 | N/S | N/S | N/S | 10 | 8 | 1661 | 364 | 3 | 0.7 | 20.35 | 3.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-03 | 2.08 | 7.3 | 5 | 9 | 5 | N/S | 7 | 8 | 1892 | 372 | 4 | 1.1 | 19.54 | 3.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-04 | 2.06 | 7.4 | 5.8 | 8 | 5 | <5 | 9 | 7 | 1882 | 366 | 4 | 1 | 20.33 | 3.36 | <0.005 | 12 | N/S | 1.1 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-05 | 2.16 | 7.4 | 5 | 7 | 3 | N/S | 8 | 6 | 1740 | 354 | 4 | 0.9 | 18.98 | 3.17 | N/S | N/S | 574 | N/S | 8000 | <0.02 | 0.047 | T/X | <0.003 | 0.011 | 0.11 | <0.05 | <0.01 | 0.019 | N/S | <0.005 | 0.019 | <0.001 | 0.035 | <0.03 | 0 | <0.03 | <6 | 133 | 47 | 525 | 3.1 | 4
2016-07-06 | 3.67 | 7.5 | 4.6 | 6 | 4 | N/S | 4 | 4 | 1255 | 280 | 3 | 0.2 | 12.37 | 1.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-07 | 3.98 | 7.3 | 6 | 4 | 3 | N/S | 4 | <4 | 1142 | 212 | 2 | 0.4 | 10.79 | 1.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-08 | 2.3 | 7.2 | 4.5 | N/S | N/S | N/S | 6 | 4 | 1304 | 244 | 2 | 0.4 | 14.67 | 1.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-09 | 2.36 | 7.4 | 4.6 | N/S | N/S | N/S | 10 | 6 | 1398 | 264 | 2 | 0.4 | 18.32 | 2.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-10 | 2.36 | 7.3 | 4.5 | 5 | 3 | N/S | 9 | 6 | 1452 | 254 | 2 | 0.4 | 18.12 | 2.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-11 | 2.35 | 7.3 | 4.3 | 7 | 4 | T/X | 9 | 6 | 1402 | 264 | 2 | 0.4 | 19.96 | 2.9 | 0.005 | <5 | N/S | 1 | 26000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-07-12 | 2.35 | 7.3 | 5 | 6 | 4 | N/S | 4 | 4 | 1230 | 232 | 2 | 0.3 | 19.51 | 2.99 | N/S | N/S | 346 | N/S | N/S | <0.02 | 0.034 | 0.004 | <0.003 | 0.008 | 0.1 | N/S | <0.01 | 0.011 | N/S | <0.005 | <0.005 | <0.001 | 0.032 | <0.03 | <0.001 | <0.03 | N/S | 93 | 37 | 382 | 3.3 | 3
2016-07-13 | 2.72 | 7.3 | 4.2 | 5 | 3 | N/S | 5 | <4 | 964 | 98 | 2 | 0.4 | 18.37 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-14 | 3.45 | 7.1 | 4.7 | T/X | T/X | N/S | 9 | 8 | 900 | 166 | 2 | 0.5 | 12.7 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-15 | 2.79 | 7.3 | 5.6 | N/S | N/S | N/S | 5 | 5 | 1011 | 198 | 2 | 0.3 | 14.6 | 2.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-16 | 2.32 | 7.3 | 5 | N/S | N/S | N/S | 14 | 7 | 1086 | 232 | 2 | 0.2 | 16.9 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-17 | 2.45 | 7.3 | 4.9 | 6 | 4 | N/S | 13 | 6 | 978 | 140 | 2 | 0.2 | 16.76 | 2.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-18 | 4.09 | 7.2 | 4.8 | 10 | 5 | <5 | 11 | 6 | 728 | 144 | 3 | 1 | 10.85 | 1.98 | <0.005 | <5 | N/S | 0.7 | 8400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-07-19 | 2.55 | 7.5 | 6.6 | 5 | 3 | N/S | 6 | 5 | 950 | 220 | 3 | 0.3 | 13.11 | 2.05 | N/S | N/S | 208 | N/S | N/S | <0.02 | 0.032 | <0.001 | <0.003 | 0.008 | 0.09 | N/S | <0.01 | 0.013 | N/S | <0.005 | 0.014 | <0.001 | 0.029 | <0.03 | <0.001 | <0.03 | N/S | 80 | 32 | 329 | 2.2 | 4
2016-07-20 | 2.42 | 7.3 | 4.7 | 4 | 3 | N/S | 5 | <4 | 1022 | 222 | 2 | 0.3 | 15.61 | 2.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-21 | 2.58 | 7.4 | 5.1 | 3 | 3 | N/S | 4 | <4 | 1064 | 178 | 1 | 0.4 | 14.78 | 2.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-22 | 4.8 | 7.2 | 4.3 | N/S | N/S | N/S | 4 | <4 | 980 | 184 | 1 | 0.1 | 10.59 | 1.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-23 | 3.65 | 7.2 | 4.4 | N/S | N/S | N/S | 6 | 4 | 1304 | 240 | 1 | 0.2 | 10.4 | 1.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-24 | 4.8 | 7.2 | 5.2 | 5 | 3 | N/S | 8 | 4 | 918 | 148 | 1 | 0.1 | 7.63 | 1.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-25 | 3.48 | 7.2 | 5.1 | 5 | 3 | <5 | 9 | 6 | 1457 | 240 | 2 | 0.2 | 7.9 | 1.4 | <0.005 | <5 | N/S | 0.6 | 6000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-07-26 | 2.25 | 7.5 | 5.5 | 8 | 5 | N/S | 21 | 16 | 1676 | 288 | 2 | 0.3 | 11.63 | 2.02 | N/S | N/S | 596 | N/S | N/S | <0.02 | 0.05 | 0.003 | <0.003 | 0.012 | 0.21 | N/S | <0.01 | 0.023 | N/S | <0.005 | <0.005 | <0.001 | 0.03 | <0.03 | <0.001 | <0.03 | N/S | 119 | 44 | 477 | 19.5 | 3
2016-07-27 | 3.22 | 7.5 | 5 | 6 | 4 | N/S | 5 | 4 | 1786 | 372 | 2 | 0.3 | 13.26 | 1.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-28 | 2.86 | 7.5 | 5.1 | 16 | 9 | N/S | 52 | 40 | 1728 | 366 | 6 | 0.3 | 14.06 | 2.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-29 | 3.82 | 7.3 | 5 | N/S | N/S | N/S | 28 | 21 | 976 | 166 | 2 | <0.1 | 9.21 | 1.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-30 | 4.41 | 7.4 | 6.1 | N/S | N/S | N/S | 15 | 11 | 688 | 116 | 2 | 0.1 | 7.38 | 1.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-07-31 | 3.77 | 7.3 | 5.2 | T/X | T/X | N/S | 12 | 8 | 804 | 124 | 2 | 0.2 | 10.17 | 1.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-01 | 3.3 | 7.4 | 5.5 | 7 | 5 | T/X | 6 | 4 | 826 | 124 | 2 | 0.3 | 12.66 | 1.84 | <0.005 | <5 | N/S | 0.7 | 800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-08-02 | 3.78 | 7.4 | 3.9 | 6 | 4 | <5 | 4 | <4 | 814 | 102 | 2 | 0.3 | 12.96 | 1.75 | N/S | N/S | 169 | N/S | N/S | <0.02 | 0.028 | <0.001 | <0.003 | 0.009 | 0.06 | 0.05 | <0.01 | 0.011 | N/S | <0.005 | 0.007 | <0.001 | 0.028 | <0.03 | <0.001 | <0.03 | N/S | 72 | 30 | 304 | 2.9 | 5
2016-08-03 | 3.14 | 7.4 | 4 | T/X | T/X | N/S | <4 | <4 | 906 | 114 | 3 | 0.3 | 13.52 | 1.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-04 | 2.99 | 7.3 | 4.1 | 6 | 3 | N/S | 7 | 6 | 1010 | 134 | 3 | 0.4 | 15.04 | 2.15 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-05 | 2.33 | 7.5 | 4.6 | N/S | N/S | N/S | 5 | 5 | 1116 | 228 | 2 | 0.3 | 18.52 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-06 | 2.32 | 7.4 | 4.8 | N/S | N/S | N/S | <4 | <4 | 1141 | 250 | 2 | 0.3 | 18.09 | 2.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-07 | 2.32 | 7.4 | 4.7 | 6 | 3 | N/S | 4 | 4 | 1101 | 224 | 2 | 0.3 | 18.82 | 2.77 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-08 | 2.32 | 7.5 | 4.5 | 5 | 3 | <5 | <4 | <4 | 1170 | 224 | 2 | 0.4 | 19.36 | 2.76 | <0.005 | <5 | N/S | 1 | 3100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-08-09 | 2.32 | 7.4 | 4.3 | 4 | <2 | N/S | 6 | 4 | 1172 | 220 | 3 | 0.3 | 19.27 | 2.74 | N/S | N/S | 309 | N/S | N/S | <0.02 | 0.041 | 0.007 | <0.003 | 0.012 | 0.08 | N/S | <0.01 | 0.007 | N/S | <0.005 | 0.008 | <0.001 | 0.034 | <0.03 | <0.001 | <0.03 | N/S | 100 | 38 | 409 | 3.5 | 4
2016-08-10 | 2.31 | 7.4 | 4.2 | 4 | <2 | N/S | 7 | 5 | 1349 | 278 | 2 | 0.4 | 19.86 | 2.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-11 | 2.34 | 7.4 | 4.9 | 5 | 2 | N/S | 5 | 5 | 1487 | 306 | 3 | 0.4 | 21.32 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-12 | 3.65 | 7.4 | 4.9 | N/S | N/S | N/S | 9 | 7 | 1158 | 234 | 3 | 0.2 | 15.28 | 2.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-13 | 4.54 | 7.4 | 5.6 | N/S | N/S | N/S | 6 | 5 | 820 | 142 | 2 | 0.1 | 7.89 | 1.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-14 | 3.89 | 7.5 | 5 | 5 | <2 | N/S | 6 | 5 | 1060 | 166 | 2 | 0.2 | 8 | 1.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-15 | 4.3 | 7.3 | 4.6 | T/X | T/X | <5 | 8 | 6 | 1233 | 344 | 3 | 0.2 | 10.56 | 1.2 | <0.005 | <5 | N/S | 0.6 | 2700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-08-16 | 4.56 | 7.3 | 4.4 | 5 | 2 | N/S | 10 | 7 | 1263 | 268 | 2 | 0.2 | 10.07 | 1.3 | N/S | N/S | 396 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.011 | 0.13 | N/S | <0.01 | 0.011 | N/S | <0.005 | <0.005 | <0.001 | 0.022 | <0.03 | <0.001 | <0.03 | N/S | 95 | 36 | 383 | 3.7 | 4
2016-08-17 | 3.75 | 7.2 | 4.7 | T/X | T/X | N/S | 7 | 6 | 1086 | 142 | 2 | 0.2 | 10.99 | 1.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-18 | 3.4 | 7.4 | 4.7 | T/X | T/X | N/S | 9 | 6 | 1281 | 178 | 3 | 0.5 | 12.33 | 1.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-19 | 2.26 | 7.4 | 4.3 | N/S | N/S | N/S | 8 | 8 | 1337 | 162 | 2 | 0.2 | 16.27 | 2.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-20 | 3.83 | 7.4 | 4.2 | N/S | N/S | N/S | 11 | 7 | 1156 | 166 | 2 | 0.3 | 13.77 | 1.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-21 | 3.85 | 7.3 | 4.6 | 5 | 3 | N/S | 10 | 6 | 1126 | 132 | 2 | 0.2 | 11.65 | 1.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-22 | 2.74 | 7.4 | 5 | 4 | <2 | <5 | 5 | 5 | 1177 | 160 | 2 | 0.5 | 14.46 | 2.28 | <0.005 | 5 | N/S | 0.8 | 300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-08-23 | 2.24 | 7.5 | 5.4 | T/X | T/X | N/S | 6 | 4 | 1344 | 210 | 2 | 0.3 | 17.7 | 2.59 | N/S | N/S | 418 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.006 | 0.07 | N/S | <0.01 | 0.007 | N/S | <0.005 | 0.006 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | N/S | 92 | 39 | 388 | 4.5 | 4
2016-08-24 | 2.56 | 7.3 | 4.3 | T/X | T/X | N/S | 4 | <4 | 1294 | 254 | 2 | 0.3 | 18.24 | 2.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-25 | 2.52 | 7.3 | 4.3 | T/X | T/X | N/S | 6 | 4 | 1090 | 170 | 3 | 0.3 | 16.85 | 2.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-26 | 2.44 | 7.3 | 5.9 | N/S | N/S | N/S | 10 | 8 | 1221 | 190 | 2 | 0.3 | 17.72 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-27 | 4.05 | 7.4 | 6 | N/S | N/S | N/S | 10 | 7 | 986 | 172 | 3 | 0.1 | 11.85 | 1.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-28 | 4.03 | 7.5 | 5.4 | 4 | <2 | N/S | 6 | 5 | 1002 | 188 | 2 | 0.3 | 8.86 | 1.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-08-29 | 3.68 | 7.4 | 4.8 | 4 | <2 | <5 | 7 | 4 | 1034 | 172 | 2 | 0.2 | 9.82 | 1.45 | <0.005 | <5 | N/S | 0.6 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-08-30 | 4.14 | 7.5 | 5 | T/X | T/X | N/S | 6 | 5 | 902 | 160 | 2 | 0.2 | 10.15 | 1.56 | N/S | N/S | 229 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.007 | 0.09 | N/S | <0.01 | 0.007 | N/S | <0.005 | 0.019 | <0.001 | 0.021 | <0.03 | <0.001 | <0.03 | N/S | 86 | 35 | 358 | 4.8 | 4
2016-08-31 | 3.34 | 7.4 | 5.8 | T/X | T/X | N/S | 6 | 6 | 1018 | 116 | 2 | 0.2 | 11.26 | 1.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-01 | 2.25 | 7.3 | 4.4 | T/X | T/X | N/S | 5 | 4 | 1378 | 238 | 2 | 0.2 | 15.93 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-02 | 2.28 | 7.4 | 4.2 | N/S | N/S | N/S | 5 | <4 | 1398 | 240 | 2 | 0.3 | 16.67 | 2.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-03 | 2.34 | 7.3 | 4.9 | N/S | N/S | N/S | 6 | <4 | 1220 | 150 | 2 | 0.2 | 17.26 | 2.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-04 | 2.31 | 7.5 | 4.9 | T/X | T/X | N/S | 4 | 4 | 1415 | 248 | 2 | 0.3 | 18.63 | 2.44 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-05 | 2.27 | 7.5 | 4.4 | T/X | T/X | <5 | <4 | 4 | 1482 | 282 | 2 | 0.3 | 18.88 | 2.57 | <0.005 | <5 | N/S | 0.9 | 4500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-06 | 2.26 | 7.5 | 4.6 | 5 | 3 | N/S | 4 | <4 | 1374 | 232 | 2 | 0.3 | 17.9 | 2.63 | N/S | N/S | 424 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.006 | 0.06 | <0.05 | <0.01 | 0.007 | N/S | <0.005 | 0.02 | <0.001 | 0.034 | <0.03 | <0.001 | 0.09 | <6 | 94 | 39 | 394 | 3.7 | 5
2016-09-07 | 2.3 | 7.5 | 4.1 | 4 | 2 | N/S | <4 | <4 | 1355 | 194 | 2 | 0.3 | 18.28 | 2.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-08 | 2.82 | 7.5 | 4.5 | 5 | 3 | N/S | 6 | <4 | 1218 | 160 | 2 | 0.5 | 16.31 | 2.39 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-09 | 2.31 | 7.5 | 5.5 | N/S | N/S | N/S | 4 | <4 | 1214 | 174 | 1 | 0.2 | 17.52 | 2.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-10 | 2.29 | 7.4 | 4.7 | N/S | N/S | N/S | 4 | <4 | 1049 | 116 | 1 | 0.3 | 18.53 | 2.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-11 | 2.26 | 7.5 | 4.2 | T/X | T/X | N/S | 4 | <4 | 980 | 90 | 2 | 0.3 | 20.59 | 2.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-12 | 2.19 | 7.4 | 4.3 | T/X | T/X | <5 | 13 | 8 | 998 | 156 | 3 | 0.5 | 20.42 | 3.35 | <0.005 | 7 | N/S | 1 | 5300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-09-13 | 2 | 7.4 | 4.9 | T/X | T/X | N/S | 17 | 12 | 1242 | 238 | 3 | 0.5 | 19.06 | 2.9 | N/S | N/S | 351 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.02 | 0.18 | N/S | <0.01 | 0.026 | N/S | <0.005 | 0.008 | <0.001 | 0.044 | <0.03 | <0.001 | <0.03 | N/S | 109 | 39 | 434 | 4.5 | 6
2016-09-14 | 1.95 | 7.4 | 4.6 | T/X | T/X | N/S | 13 | 10 | 1529 | 386 | 3 | 0.3 | 18.21 | 2.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-15 | 1.97 | 7.3 | 4 | 9 | 5 | N/S | 9 | 6 | 1491 | 258 | 3 | 0.2 | 19.04 | 2.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-16 | 1.82 | 7.7 | 6.5 | N/S | N/S | N/S | 8 | 6 | 1526 | 282 | 3 | 0.2 | 20.69 | 3.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-17 | 2.13 | 7.3 | 4.4 | N/S | N/S | N/S | 9 | 8 | 1597 | 300 | 3 | 0.2 | 21.5 | 3.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-18 | 2.06 | 7.6 | 4.7 | 9 | 5 | N/S | 12 | 12 | 1776 | 312 | 3 | 0.2 | 20.83 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-19 | 2 | 7.5 | 3.8 | 6 | 3 | <5 | 8 | 5 | 1817 | 310 | 2 | 0.3 | 20.69 | 3.37 | <0.005 | <5 | N/S | 1.1 | 1700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-09-20 | 2.17 | 7.4 | 4.1 | T/X | T/X | N/S | 10 | 6 | 1931 | 340 | 2 | 0.3 | 18.53 | 3.28 | N/S | N/S | 705 | N/S | N/S | <0.02 | 0.043 | 0.001 | <0.003 | 0.028 | 0.12 | N/S | <0.01 | 0.012 | N/S | <0.005 | 0.019 | <0.001 | 0.04 | <0.03 | <0.001 | 0.03 | N/S | 125 | 43 | 492 | 2.4 | 4
2016-09-21 | 2.28 | 7.2 | 2.9 | T/X | T/X | N/S | 6 | 4 | 1862 | 302 | 2 | 0.3 | 18.58 | 2.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-22 | 2.26 | 7.4 | 5.2 | T/X | T/X | N/S | 14 | 12 | 1696 | 246 | 2 | 0.3 | 19 | 3.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-23 | 2.23 | 7.5 | 5.4 | N/S | N/S | N/S | 10 | 6 | 1761 | 344 | 2 | 0.2 | 22.89 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-24 | 2.17 | 7.5 | 6.8 | N/S | N/S | N/S | 12 | 8 | 1686 | 328 | 2 | 0.2 | 23.18 | 3.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-25 | 2 | 7.4 | 6.2 | 6 | 3 | N/S | 10 | 7 | 1682 | 358 | 2 | 0.3 | 22.39 | 3.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-26 | 1.92 | 7.6 | 4.3 | 5 | 4 | <5 | 14 | 8 | 1472 | 242 | 2 | 0.3 | 21.22 | 3.11 | <0.005 | <5 | N/S | 1.1 | 200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-09-27 | 1.9 | 7.6 | 5.6 | 6 | 3 | N/S | 12 | 9 | 1560 | 274 | 3 | 0.2 | 21.67 | 3.08 | N/S | N/S | 500 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.011 | 0.13 | N/S | <0.01 | 0.01 | N/S | <0.005 | 0.009 | <0.001 | 0.046 | <0.03 | <0.001 | <0.03 | N/S | 109 | 40 | 437 | 3.5 | 5
2016-09-28 | 1.86 | 7.5 | 5.6 | 3 | 2 | N/S | <4 | <4 | 1354 | 166 | 2 | 0.2 | 22.94 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-29 | 2.15 | 7.5 | 5.3 | 6 | 2 | N/S | 11 | 7 | 1201 | 186 | 3 | 0.2 | 20.49 | 2.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-09-30 | 2.93 | 7.5 | 6.5 | N/S | N/S | N/S | 22 | 16 | 896 | 170 | 4 | 0.5 | 16.89 | 2.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-01 | 3.47 | 7.5 | 5.4 | N/S | N/S | N/S | 22 | 16 | 588 | 166 | 3 | 0.1 | 13.4 | 1.79 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-02 | 4.28 | 7.3 | 5.1 | 8 | 5 | N/S | 18 | 14 | 764 | 122 | 2 | 0.1 | 11.32 | 1.41 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-03 | 2.56 | 7.4 | 6.5 | T/X | T/X | <5 | 6 | <4 | 848 | 120 | 2 | 0.1 | 13.29 | 1.52 | <0.005 | 6 | N/S | 0.7 | 500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-10-04 | 2.21 | 7.6 | 5.9 | 3 | <2 | N/S | 4 | <4 | 1028 | 194 | 2 | 0.1 | 17.63 | 2.02 | N/S | N/S | 250 | N/S | N/S | <0.02 | 0.029 | <0.001 | <0.003 | 0.009 | 0.07 | <0.05 | <0.01 | 0.004 | N/S | <0.005 | <0.005 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | N/S | 85 | 34 | 353 | 5.4 | 6
2016-10-05 | 2.3 | 7.6 | 5.2 | T/X | T/X | N/S | 6 | 4 | 1262 | 264 | 2 | 0.2 | 19.52 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-06 | 3.35 | 7.4 | 5.6 | 3 | 3 | N/S | <4 | <4 | 1014 | 192 | 2 | 0.1 | 16.06 | 1.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-07 | 4.19 | 7.3 | 5.8 | N/S | N/S | N/S | 28 | 21 | 994 | 226 | 4 | 0.1 | 14.44 | 2.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-08 | 2.82 | 7.4 | 5.6 | N/S | N/S | N/S | 14 | 9 | 954 | 190 | 3 | 0.1 | 13.58 | 1.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-09 | 2.27 | 7.5 | 6.5 | T/X | T/X | N/S | 15 | 11 | 1012 | 162 | 3 | 0.2 | 17.12 | 2.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-10 | 2.34 | 7.4 | 5.9 | 7 | 3 | <5 | 7 | 6 | 1028 | 132 | 3 | 0.7 | 17.39 | 2.36 | <0.005 | <5 | N/S | 0.9 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-10-11 | 2.22 | 7.4 | 6.2 | T/X | T/X | N/S | <4 | <4 | 1052 | 128 | 2 | 0.3 | 18.1 | 2.32 | N/S | N/S | 282 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.011 | 0.06 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.012 | <0.001 | 0.037 | <0.03 | <0.001 | <0.03 | N/S | 91 | 36 | 375 | 3.5 | 5
2016-10-12 | 2.16 | 7.3 | 5.3 | T/X | T/X | N/S | <4 | <4 | 960 | 104 | 1 | 0.1 | 18.3 | 2.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-13 | 2.65 | 7.4 | 6 | T/X | T/X | N/S | 8 | 6 | 878 | 130 | 2 | 0.2 | 16.01 | 2.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-14 | 2.2 | 7.4 | 7.1 | N/S | N/S | N/S | 11 | 6 | 890 | 122 | 1 | 0.3 | 18.09 | 2.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-15 | 2.18 | 7.3 | 5 | N/S | N/S | N/S | 4 | 4 | 926 | 124 | 2 | 0.2 | 20.72 | 2.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-16 | 3.15 | 7.3 | 5.4 | 8 | 2 | N/S | 9 | 6 | 758 | 120 | 2 | 0.7 | 16.46 | 2.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-17 | 2.34 | 7.3 | 5.1 | T/X | T/X | <5 | <4 | <4 | 772 | 112 | 2 | 0.3 | 15.47 | 1.92 | <0.005 | <5 | N/S | 0.7 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-10-18 | 2.35 | 7.4 | 4.1 | T/X | T/X | N/S | 6 | 4 | 1247 | 292 | 2 | 0.2 | 17.44 | 2.23 | N/S | N/S | 194 | N/S | N/S | <0.02 | 0.03 | <0.001 | <0.003 | 0.007 | 0.09 | N/S | <0.01 | 0.007 | N/S | <0.005 | 0.01 | <0.001 | 0.033 | <0.03 | <0.001 | <0.03 | N/S | 77 | 31 | 322 | 4.7 | 5
2016-10-19 | 2.17 | 7.5 | 6.7 | T/X | T/X | N/S | <4 | <4 | 780 | 18 | 2 | 0.2 | 20.32 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-20 | 2.13 | 7.4 | 5.3 | T/X | T/X | N/S | 4 | <4 | 802 | 20 | 2 | 0.2 | 22.55 | 2.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-21 | 1.92 | 7.3 | 5.8 | N/S | N/S | N/S | 7 | 4 | 870 | 116 | 2 | 0.2 | 23.32 | 2.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-22 | 1.85 | 7.4 | 5.6 | N/S | N/S | N/S | 5 | 4 | 890 | 112 | 1 | 0.2 | 23.65 | 2.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-23 | 1.89 | 7.5 | 5.9 | T/X | T/X | N/S | 5 | 4 | 886 | 78 | 1 | 0.2 | 22.21 | 2.82 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-24 | 1.84 | 7.4 | 5.5 | T/X | T/X | <5 | 5 | <4 | 856 | 122 | 2 | 0.3 | 22.92 | 2.95 | <0.005 | <5 | N/S | 1 | T/X | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-10-25 | 1.71 | 7.4 | 6.2 | T/X | T/X | N/S | 7 | 4 | 912 | 156 | 2 | 0.2 | 24.49 | 3.06 | N/S | N/S | 168 | N/S | N/S | <0.02 | 0.031 | <0.001 | <0.003 | 0.008 | 0.08 | N/S | <0.01 | 0.009 | N/S | <0.005 | 0.015 | <0.001 | 0.042 | <0.03 | <0.001 | <0.03 | N/S | 82 | 31 | 333 | 2.7 | 6
2016-10-26 | 2.58 | 7.4 | 5.8 | T/X | T/X | N/S | 20 | 17 | 812 | 170 | 3 | <0.1 | 21.35 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-27 | 3.85 | 7.2 | 6 | T/X | T/X | N/S | 11 | 7 | 728 | 166 | 2 | <0.1 | 11.55 | 1.38 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-28 | 2.92 | 7.4 | 4.9 | N/S | N/S | N/S | <4 | <4 | 832 | 158 | 1 | 0.2 | 10.83 | 1.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-29 | 2.98 | 7.3 | 5.1 | N/S | N/S | N/S | 5 | <4 | 1015 | 180 | 1 | 0.4 | 14.96 | 1.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-30 | 2.79 | 7.4 | 5.3 | <2 | <2 | N/S | <4 | <4 | 940 | 136 | 1 | 0.4 | 16.96 | 1.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-10-31 | 2.33 | 7.4 | 5 | T/X | T/X | <5 | 4 | <4 | 872 | 100 | 2 | 0.3 | 18.12 | 2.25 | <0.005 | <5 | N/S | 0.8 | 2800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-11-01 | 2.44 | 7.4 | 5.9 | 4 | <2 | N/S | 6 | 4 | 852 | 112 | 2 | 0.3 | 19.32 | 2.56 | N/S | N/S | 185 | N/S | N/S | <0.02 | 0.028 | <0.001 | <0.003 | 0.008 | 0.1 | <0.05 | <0.01 | 0.007 | N/S | <0.005 | <0.005 | <0.001 | 0.032 | <0.03 | <0.001 | <0.03 | N/S | 76 | 32 | 322 | 2.7 | 6
2016-11-02 | 2.94 | 7.4 | 5.3 | 4 | 3 | N/S | 8 | 5 | 814 | 108 | 2 | 0.8 | 17.86 | 2.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-03 | 3.44 | 7.4 | 5 | T/X | T/X | N/S | 4 | <4 | 876 | 156 | 2 | 0.7 | 15.02 | 1.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-04 | 3.08 | 7.5 | 5.5 | N/S | N/S | N/S | 8 | 7 | 924 | 140 | 2 | 0.1 | 15.16 | 1.89 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-05 | 2.72 | 7.4 | 5.3 | N/S | N/S | N/S | 7 | 5 | 964 | 120 | 2 | 0.3 | 16.79 | 2.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-06 | 2.42 | 7.4 | 5 | 3 | 2 | N/S | 6 | 4 | 1002 | 144 | 2 | 0.2 | 18.66 | 2.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-07 | 2.24 | 7.4 | 5.2 | 6 | <2 | <5 | 4 | <4 | 1072 | 204 | 2 | 0.2 | 19.16 | 2.71 | <0.005 | <5 | N/S | 0.9 | 800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-11-08 | 2.27 | 7.5 | 5.6 | 3 | <2 | N/S | 6 | 4 | 1110 | 208 | 2 | 0.2 | 19.37 | 2.65 | N/S | N/S | 302 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.011 | 0.09 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.022 | <0.001 | 0.033 | <0.03 | <0.001 | <0.03 | N/S | 96 | 37 | 389 | 1.5 | 5
2016-11-09 | 2.26 | 7.4 | 6 | T/X | T/X | N/S | 10 | 6 | 1172 | 180 | 2 | 0.1 | 20.93 | 2.92 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-10 | 2.24 | 7.5 | 6.2 | 3 | <2 | N/S | 6 | 5 | 1127 | 156 | 2 | 0.1 | 19.75 | 2.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-11 | 2.23 | 7.5 | 4.3 | N/S | N/S | N/S | 4 | <4 | 1160 | 132 | 2 | 0.1 | 20 | 2.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-12 | 2.21 | 7.5 | 4.8 | N/S | N/S | N/S | <4 | <4 | 1182 | 146 | 2 | 0.1 | 20.72 | 3.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-13 | 2.2 | 7.4 | 5 | T/X | T/X | N/S | <4 | <4 | 1187 | 120 | 2 | 0.1 | 20.68 | 3.14 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-14 | 2.2 | 7.4 | 5.2 | T/X | T/X | <5 | 4 | <4 | 1135 | 158 | 2 | 0.2 | 20.11 | 3.09 | <0.005 | <5 | N/S | 1.1 | 400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-11-15 | 2.22 | 7.4 | 5.7 | T/X | T/X | N/S | 5 | 5 | 1026 | 148 | 3 | 0.2 | 19.56 | 3.14 | N/S | N/S | 268 | N/S | N/S | <0.02 | 0.031 | <0.001 | <0.003 | 0.008 | 0.09 | N/S | <0.01 | 0.009 | N/S | <0.005 | 0.016 | <0.001 | 0.037 | <0.03 | <0.001 | <0.03 | N/S | 82 | 34 | 343 | 4.3 | 6
2016-11-16 | 2.23 | 7.4 | 6 | T/X | T/X | N/S | 4 | <4 | 980 | 142 | 2 | 0.2 | 19.69 | 3.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-17 | 2.2 | 7.4 | 5.5 | T/X | T/X | N/S | 14 | 11 | 938 | 122 | 3 | 0.2 | 19.65 | 3.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-18 | 2.12 | 7.4 | 5.6 | N/S | N/S | N/S | 6 | 5 | 904 | 152 | 2 | 0.2 | 19.3 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-19 | 2.17 | 7.3 | 7.1 | N/S | N/S | N/S | 4 | <4 | 880 | 180 | 2 | 0.2 | 19.61 | 3.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-20 | 2.22 | 7.5 | 7.5 | 7 | 3 | N/S | 5 | 4 | 888 | 106 | 2 | 0.3 | 19.4 | 3.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-21 | 2.18 | 7.3 | 5.1 | 4 | <2 | <5 | 5 | <4 | 892 | 126 | 2 | 0.2 | 23.16 | 3.15 | <0.005 | <5 | N/S | 1 | 700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-11-22 | 2.16 | 7.4 | 6.3 | 4 | 2 | N/S | <4 | <4 | 874 | 102 | 1 | 0.2 | 23.81 | 3.12 | N/S | N/S | 176 | N/S | N/S | <0.02 | 0.027 | <0.001 | <0.003 | 0.007 | 0.06 | N/S | <0.01 | 0.004 | N/S | <0.005 | 0.01 | <0.001 | 0.033 | <0.03 | <0.001 | <0.03 | N/S | 77 | 30 | 316 | 3.4 | 6
2016-11-23 | 2.35 | 7.4 | 5.5 | 3 | <2 | N/S | <4 | <4 | 850 | 136 | 2 | 0.3 | 15.78 | 3.08 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-24 | 2.6 | 7.3 | 6 | 6 | <2 | N/S | <4 | <4 | 832 | 136 | 2 | 0.4 | 18.97 | 2.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-25 | 2.21 | 7.3 | 5.9 | N/S | N/S | N/S | <4 | <4 | 864 | 152 | 1 | 0.2 | 19.07 | 2.55 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-26 | 2.43 | 7.3 | 6.4 | N/S | N/S | N/S | <4 | <4 | 854 | 158 | 2 | 0.9 | 20.06 | 2.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-27 | 2.19 | 7.3 | 5.4 | 4 | <2 | N/S | <4 | <4 | 892 | 122 | 2 | 0.4 | 21.93 | 2.88 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-11-28 | 3.99 | 7.2 | 5.8 | 9 | <2 | <5 | 4 | <4 | 718 | 90 | 4 | 3.3 | 14.23 | 2.25 | <0.005 | 5 | N/S | 0.8 | 3500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-11-29 | 4.56 | 7.2 | 5.5 | 2 | <2 | N/S | 6 | 5 | 550 | 78 | 1 | 0.2 | 9.79 | 1.12 | N/S | N/S | 108 | N/S | N/S | <0.02 | 0.022 | <0.001 | <0.003 | 0.005 | 0.07 | N/S | <0.01 | 0.005 | N/S | <0.005 | <0.005 | <0.001 | 0.016 | <0.03 | <0.001 | <0.03 | N/S | 62 | 26 | 261 | 3.3 | 5
2016-11-30 | 3 | 7.4 | 6.4 | 3 | <2 | N/S | <4 | <4 | 646 | 112 | 1 | 0.3 | 12.27 | 1.29 | N/S | N/S | 119 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-01 | 3.25 | 7.3 | 6.3 | 5 | 3 | N/S | 7 | 6 | 694 | 100 | 1 | 0.1 | 13.66 | 1.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-02 | 3.33 | 7.4 | 6.6 | N/S | N/S | N/S | 5 | 4 | 758 | 122 | 1 | 0.1 | 14.62 | 1.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-03 | 2.57 | 7.4 | 7 | N/S | N/S | N/S | <4 | <4 | 778 | 124 | 2 | 0.3 | 16.45 | 2.06 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-04 | 2.57 | 7.3 | 5.8 | 4 | 2 | N/S | <4 | <4 | 876 | 102 | 2 | 0.7 | 17.93 | 2.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-05 | 2.63 | 7.3 | 5.3 | 7 | <2 | <5 | 5 | 4 | 1168 | 166 | 2 | 0.7 | 16.18 | 2.06 | 0.006 | 8 | 385 | 0.9 | 600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-06 | 2.87 | 7.3 | 6.1 | 6 | 3 | N/S | 6 | 4 | 1185 | 132 | 2 | 0.2 | 15.06 | 1.86 | N/S | N/S | 395 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.007 | 0.08 | <0.05 | <0.01 | 0.007 | N/S | <0.005 | 0.007 | <0.001 | 0.027 | <0.03 | <0.001 | <0.03 | N/S | 90 | 37 | 376 | 2.1 | 4
2016-12-07 | 2.93 | 7.4 | 7 | 6 | 3 | N/S | 4 | <4 | 1084 | 130 | 2 | 0.2 | 15.77 | 1.78 | N/S | N/S | 329 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-12-08 | 2.22 | 7.3 | 6.6 | 3 | 3 | N/S | 5 | <4 | 1006 | 140 | 2 | 0.1 | 15.73 | 1.89 | N/S | N/S | 266 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-09 | 2.54 | 7.3 | 6.7 | N/S | N/S | N/S | <4 | <4 | 692 | 114 | 1 | 0.1 | 17.44 | 2.09 | N/S | N/S | 221 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-10 | 2.19 | 7.4 | 6.6 | N/S | N/S | N/S | 14 | 10 | 946 | 94 | 2 | <0.1 | 17.66 | 2.42 | N/S | N/S | 225 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-11 | 2.58 | 7.4 | 6.7 | T/X | T/X | N/S | <4 | <4 | 1110 | 104 | 2 | 0.9 | 17.06 | 2.33 | N/S | N/S | 322 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-12 | 2.51 | 7.3 | 7.1 | 3 | <2 | <5 | <4 | <4 | 1602 | 150 | 2 | 0.6 | 17.13 | 2.27 | 0.008 | <5 | 586 | 0.9 | 600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-12-13 | 2.16 | 7.3 | 6.8 | <2 | <2 | N/S | <4 | <4 | 1512 | 152 | 1 | 0.3 | 17.95 | 2.26 | N/S | N/S | 570 | N/S | N/S | <0.02 | 0.041 | <0.001 | <0.003 | 0.005 | <0.05 | N/S | <0.01 | 0.004 | N/S | <0.005 | 0.019 | <0.001 | 0.025 | <0.03 | <0.001 | <0.03 | N/S | 97 | 39 | 403 | 1.9 | 4
2016-12-14 | 1.98 | 7.3 | 7.5 | 3 | 2 | N/S | <4 | <4 | 1321 | 160 | 2 | 0.2 | 20.56 | 2.55 | N/S | N/S | 436 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-15 | 2.23 | 7.3 | 7.8 | 5 | 2 | N/S | 5 | <4 | 1148 | 148 | 1 | 0.1 | 21.43 | 2.58 | N/S | N/S | 354 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-16 | 2.21 | 7.3 | 6.7 | N/S | N/S | N/S | 4 | 4 | 1095 | 160 | 2 | 0.1 | 20.98 | 2.65 | N/S | N/S | 296 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-17 | 2.2 | 7.2 | 6 | N/S | N/S | N/S | 5 | 4 | 1061 | 188 | 1 | 0.2 | 21.76 | 2.84 | N/S | N/S | 277 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-18 | 2.19 | 7.2 | 6.3 | 8 | 3 | N/S | 6 | 4 | 1134 | 108 | 2 | 0.2 | 22.73 | 3.05 | N/S | N/S | 322 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-19 | 2.12 | 7.2 | 6.6 | 8 | 5 | <5 | 6 | 5 | 1090 | 130 | 2 | 0.2 | 21.73 | 2.92 | <0.005 | <5 | 318 | 1 | 700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2016-12-20 | 1.97 | 7.3 | 6.8 | 10 | 4 | N/S | 9 | 6 | 1056 | 152 | 2 | 0.2 | 19.29 | 2.69 | N/S | N/S | 288 | N/S | N/S | <0.02 | 0.036 | <0.001 | <0.003 | 0.008 | 0.08 | N/S | <0.01 | 0.011 | N/S | <0.005 | <0.005 | <0.001 | 0.034 | <0.03 | <0.001 | <0.03 | N/S | 87 | 36 | 365 | 2.9 | 7
2016-12-21 | 1.92 | 7.4 | 6.7 | 8 | 4 | N/S | 7 | 5 | 1060 | 178 | 2 | 0.2 | 18.3 | 2.48 | N/S | N/S | 285 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-22 | 2.04 | 7.3 | 6.3 | 7 | 3 | N/S | 6 | 5 | 1046 | 118 | 2 | 0.5 | 19.22 | 2.67 | N/S | N/S | 290 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-23 | 1.96 | 7.2 | 6.2 | N/S | N/S | N/S | 6 | 6 | 1152 | 130 | 2 | 0.3 | 19.04 | 2.67 | N/S | N/S | 331 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-24 | 2.24 | 7.3 | 5.9 | N/S | N/S | N/S | 6 | 5 | 1416 | 142 | 3 | 1 | 16.91 | 2.44 | N/S | N/S | 502 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-25 | 2.41 | 7.2 | 6 | 9 | 2 | N/S | 6 | 6 | 1528 | 158 | 4 | 1.7 | 14.32 | 2.23 | N/S | N/S | 585 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-26 | 4.4 | 7.2 | 4.8 | 13 | 7 | <5 | 12 | 10 | 1555 | 172 | 3 | 1.5 | 10.29 | 1.41 | 0.006 | <5 | 634 | 0.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-27 | 3.95 | 7.2 | 5.9 | 9 | 6 | N/S | 12 | 9 | 1430 | 218 | 2 | 0.2 | 8.88 | 0.98 | N/S | N/S | 555 | N/S | 1200 | <0.02 | 0.046 | <0.001 | <0.003 | 0.008 | 0.09 | N/S | <0.01 | 0.012 | N/S | <0.005 | 0.008 | <0.001 | 0.024 | <0.03 | <0.001 | <0.03 | <6 | 97 | 39 | 405 | 2.3 | 4
2016-12-28 | 2.61 | 7.3 | 6.1 | 8 | 4 | N/S | 5 | 4 | 1288 | 86 | 2 | 0.6 | 11.35 | 1.33 | N/S | N/S | 476 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-29 | 3.36 | 7.3 | 6.8 | 7 | 3 | N/S | 4 | <4 | 1242 | 154 | 3 | 1 | 12.04 | 1.45 | N/S | N/S | 433 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-30 | 2.58 | 7.3 | 6.8 | N/S | N/S | N/S | 5 | 4 | 1190 | 150 | 2 | 0.5 | 14.75 | 1.65 | N/S | N/S | 402 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2016-12-31 | 2.61 | 7.4 | 7.9 | N/S | N/S | N/S | 10 | 8 | 1102 | 148 | 4 | 1.6 | 16.57 | 2.34 | N/S | N/S | 330 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
PQL eff. Jan1-Apr31, 2016 |  |  |  | 2 | 2 | 5 | 4 | 4 | 100 |  | 1 | 0.1 | 0.15 | 0.1 | 0.005 | 5 | 5 | 0.1
PQL eff. May1-Dec31, 2016 |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 |  | 1 | 0.1 | 0.15 | 0.1 | 0.005 | 5 | 5 | 0.1
PQL eff. Jan1-Jun30, 2016 | [19 empty] | 0.05 | 0.004 | 0.001 | 0.005 | 0.005 | 0.1 | 0.1 | 0.02 | 0.001 | 0.2 | 0.005 | 0.005 | 0.001 | 0.01 | 0.05 | 0.001 | 0.1 | 6 | 1 | 1 |  | 0.5 | 1
PQL eff. Jul1-Dec31, 2016 | [19 empty] | 0.02 | 0.002 | 0.001 | 0.003 | 0.004 | 0.05 | 0.05 | 0.01 | 0.001 | 0.05 | 0.005 | 0.005 | 0.001 | 0.005 | 0.03 | 0.001 | 0.03 | 6 | 1 | 1 |  | 0.5 | 1
Observations | 366 | 366 | 366 | 195 | 196 | 50 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 366 | 51 | 52 | 182 | 52 | 49 | 52 | 52 | 51 | 52 | 52 | 52 | 12 | 52 | 52 | 0 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 47 | 52
Minimum | 1.71 | 7.1 | 2.9 | <2 | <2 | <5 | <4 | <4 | 542 | 18 | 1 | <0.1 | 5.1 | 0.78 | <0.005 | <5 | <10 | 0.5 | 200 | <0.02 | 0.022 | <0.001 | <0.003 | 0.005 | <0.05 | <0.05 | <0.01 | 0.003 |  | <0.005 | <0.005 | <0.001 | 0.015 | <0.03 | <0.001 | <0.03 | <6 | 62 | 26 | 261 | 1.5 | 3
Mean | 2.74 | 7.4 | 5.9 | <10 | <5 | <5 | <10 | <8 | 1179 | 177 | 3 | <1.3 | 15.29 | 2.28 | <0.005 | <6 | <406 | 0.9 | 23490 | <0.03 | 0.039 | <0.002 | <0.004 | 0.011 | <0.11 | <0.08 | <0.01 | 0.014 |  | <0.005 | <0.011 | <0.001 | 0.031 | <0.04 | <0.001 | <0.06 | <6 | 95 | 38 | 393 | 11.6 | 5
Maximum | 4.8 | 7.7 | 10 | 29 | 20 | <5 | 52 | 40 | 1931 | 386 | 17 | 13.7 | 24.49 | 3.77 | 0.011 | 12 | 824 | 1.1 | 310000 | <0.05 | 0.05 | 0.016 | <0.005 | 0.028 | 0.25 | <0.10 | <0.02 | 0.043 |  | <0.005 | 0.066 | 0.001 | 0.057 | <0.05 | <0.001 | <0.10 | 15 | 133 | 47 | 525 | 250.2 | 8
Std Dev | 0.7 | 0.1 | 1.4 | 6 | 3 | 0 | 7 | 5 | 266 | 64 | 2 | 2.1 | 4.12 | 0.63 | 0.001 | 4 | 130 | 0.2 | 49581 | 0.02 | 0.007 | 0.003 | 0.001 | 0.005 | 0.05 | 0.03 | 0.01 | 0.01 |  | 0 | 0.01 | 0 | 0.009 | 0.01 | 0 | 0.04 | 1 | 14 | 4 | 51 | 37.7 | 1
JANUARY 4, 2016 FOG: Batch LCS Failure.
JANUARY 3 - 7, 10, 2016 BOD5, CBOD5, T/X: Expired BOD nutrient used.
JANUARY 5, 12, 19, 2016 LL Hg, T/X: Field Blank failure.
JANUARY 11, 2016 Phenol: Sample MS recovery failed, but LCS passed.
JANUARY 11,18, 20, 2016 BOD5, CBOD5, T/X: Method Blank failure.
JANUARY 13, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
JANUARY 17, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
JANUARY 18, 2016 FOG_TP: Sample MS recovery failed, but LCS passed.
JANUARY 30, 2016 NH3-N: Sample MS recovery failed, but LCS passed.
FEBRUARY 10, 17, 26, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
MARCH 4, 17, 2016 TKN: Sample MS recovery failed, but LCS passed.
MARCH 8, 2016 LL Hg, T/X: Field Blank failure.
MARCH 8, 21, 23, 31, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
MARCH 17, 2016 Tol Phos: Sample MS recovery failed, but LCS passed.
MARCH 29, 2016 LL Hg, T/X: Sample analzed next day.
APRIL 12, 2016 NO2+NO3-N; T/X: Result unconfirmed due to insufficient sample volume.
APRIL 13, 2015 BOD5, CBOD5, T/X: Method blank failure.
APRIL 21, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
APRIL 26, 2016 LL Hg, T/X: Field Blank failure.
APRIL 26, 2015 BOD5, T/X: Improper dilution.
MAY 3, 2016 Hg: Aliquot not preserved; added prior to analysis.
MAY 15, 29, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
MAY 17, 23, 24, 2016 BOD5, CBOD5, T/X: Method blank failure.
JUNE 1, 5, 8, 2016 BOD5, CBOD5, T/X: Method blank failure.
JUNE 13, 2016 TOT-CN, T/X: Expired check stock solution.KFI.
JUNE 22, 2016 BOD5, CBOD5, T/X: LCS failure.
JULY 5, 2016 Cd, T/X: Three Tests , none within precision limits.
JULY 10, 2016 NH3_N: Sample MS recovery failed, but LCS passed.
JULY 10, 217, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
JULY 11, 2016 FOG, T/X: Batch LCS failure.
JULY 14, 31, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
AUGUST 3, 2016 BOD5, CBOD5, T/X: Method blank failure.
AUGUST 15, 17, 18, 23, 24, 25, 30, 31 2016 BOD5, CBOD5, T/X: Batch LCS failure.
SEPTEMBER 1, 4, 5, 11, 12, 13, 14, 20, 21,22, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
SEPTEMBER 3, 14, 18, 22, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
SEPTEMBER 5, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
OCTOBER 1, 7, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
OCTOBER 3, 5, 9, 11, 12, 13, 17, 18, 19, 20, 23, 25, 26, 27, 31,, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
OCTOBER 10, 17, 24, 2016, Fecal Coli; T/X: Suspected inhibition growth by media reagent.
OCTOBER 12, 2016 TKN: Sample MS recovery failed, but LCS passed.
OCTOBER 24, 2016 BOD5, CBOD5, T/X: Method blank failure.
NOVEMBER 2, 4, 13, 14, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
NOVEMBER 3, 9, 13-17, 2016 BOD5, CBOD5, T/X: Batch LCS failure.
NOVEMBER 6, 2016 TKN: Sample MS recovery failed, but LCS passed.
DECEMBER 11, 2016 BOD5, CBOD5, T/X: Method blank failure.
DECEMBER 14, 2016 NO2+NO3-N: Sample MS recovery failed, but LCS passed.

## Lemont Outfall 2017
| Flow | pH | D.O. | BOD5 | CBOD5 | FOG | SS | VSS | TS | TVS | TKN | NH3-N | NO2-N + NO3-N | P-TOT | CN | Phenol | CL | F | FEC COL | As | Ba | Cd | Cr | Cu | Fe | Fe-S | Pb | Mn | Hg | Ni | Se | Ag | Zn | Sb | Be | Tl | Cr6+ | Ca | Mg | Hardness | Hg LL | TOC
Date | MGD |  | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ug/L | mg/L | mg/L | CFU/100ml | mg/l | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | ug/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | ng/L | mg/L
2017-01-01 | 2.04 | 7.3 | 6.2 | 5 | 3 | N/S | 5 | 4 | 1033 | 120 | 3 | 0.3 | 18.27 | 2.56 | N/S | N/S | 290 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-02 | 2.06 | 7.4 | 6.3 | 5 | 3 | <5 | 5 | <4 | 1006 | 166 | 2 | 0.2 | 21.76 | 2.77 | <0.005 | T/X | 271 | 0.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-03 | 2.09 | 7.3 | 6.4 | 6 | 3 | N/S | 6 | 5 | 1057 | 122 | 2 | 0.2 | 20.98 | 2.8 | N/S | N/S | 282 | N/S | 1500 | <0.02 | 0.036 | <0.001 | <0.003 | 0.008 | 0.07 | <0.05 | <0.01 | 0.008 | N/S | <0.005 | <0.005 | <0.001 | 0.036 | <0.03 | <0.001 | <0.03 | N/S | 88 | 38 | 379 | 1.4 | 5
2017-01-04 | 2.11 | 7.3 | 7.5 | 6 | 3 | N/S | 6 | 5 | 1090 | 134 | 2 | 0.2 | 21.62 | 2.53 | N/S | N/S | 309 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-01-05 | 2.11 | 7.3 | 6.7 | 5 | 3 | N/S | 6 | 4 | 1088 | 154 | 2 | 0.2 | 21.25 | 2.43 | N/S | N/S | 294 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-06 | 2.08 | 7.3 | 6.9 | N/S | N/S | N/S | 6 | 5 | 1084 | 164 | 2 | 0.2 | 19.05 | 2.45 | N/S | N/S | 276 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-07 | 2.08 | 7.3 | 7.7 | N/S | N/S | N/S | 6 | 4 | 1078 | 198 | 2 | 0.1 | 21.5 | 2.53 | N/S | N/S | 262 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-08 | 2.09 | 7.3 | 7.5 | 6 | 3 | N/S | 7 | 5 | 1086 | 202 | 2 | 0.1 | 21.94 | 2.51 | N/S | N/S | 265 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-09 | 2.09 | 7.4 | 7.1 | T/X | T/X | <5 | 7 | 5 | 1050 | 174 | 2 | 0.2 | 22.47 | 2.64 | <0.005 | 5 | 273 | 1 | 1000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-01-10 | 1.95 | 7.3 | 6.2 | 4 | 3 | N/S | 6 | 4 | 1185 | 202 | 2 | 0.1 | 20.23 | 2.69 | N/S | N/S | 330 | N/S | N/S | <0.02 | 0.039 | <0.001 | <0.003 | 0.007 | 0.07 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.015 | <0.001 | 0.034 | <0.03 | <0.001 | <0.03 | N/S | 95 | 36 | 385 | 5.3 | 5
2017-01-11 | 2.6 | 7.2 | 7.3 | 8 | 4 | N/S | 8 | 7 | 1134 | 158 | 2 | 0.2 | 18.48 | 2.36 | N/S | N/S | 370 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-12 | 3.03 | 7.2 | 5.5 | 5 | <2 | N/S | <4 | <4 | 1153 | 146 | 2 | 0.5 | 14.51 | 1.75 | N/S | N/S | 408 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-13 | 2.2 | 7.2 | 7.3 | N/S | N/S | N/S | 5 | 4 | 830 | 94 | 1 | 0.1 | 16.52 | 1.81 | N/S | N/S | 439 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-14 | 2.18 | 7.4 | 6.4 | N/S | N/S | N/S | 5 | 4 | 920 | 118 | 1 | 0.1 | 18.44 | 2.17 | N/S | N/S | 423 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-15 | 2.15 | 7.2 | 7.8 | 5 | <2 | N/S | 4 | <4 | 850 | 128 | 1 | 0.1 | 19.33 | 2.42 | N/S | N/S | 405 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-16 | 3.04 | 7.3 | 6.5 | 7 | 3 | <5 | 6 | 5 | 1280 | 170 | 2 | 0.2 | 16.3 | 2.1 | <0.005 | <5 | 463 | 0.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-17 | 4.43 | 7.2 | 6 | T/X | T/X | N/S | 16 | 12 | 1054 | 146 | 2 | 0.4 | 8.29 | 1.22 | N/S | N/S | 387 | N/S | 3600 | <0.02 | 0.032 | <0.001 | <0.003 | 0.01 | 0.12 | N/S | <0.01 | 0.017 | N/S | <0.005 | <0.005 | <0.001 | 0.025 | <0.03 | <0.001 | <0.03 | <6 | 70 | 28 | 291 | 3.4 | 4
2017-01-18 | 3.21 | 7.2 | 7.6 | 3 | 2 | N/S | 5 | 4 | 1092 | 172 | 2 | 0.1 | 9.22 | 0.98 | N/S | N/S | 385 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-19 | 3.15 | 7.3 | 7.4 | 3 | <2 | N/S | <4 | <4 | 1165 | 140 | 1 | 0.1 | 10.38 | 1.24 | N/S | N/S | 441 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-20 | 4.72 | 7.2 | 6.9 | N/S | N/S | N/S | <4 | <4 | 1116 | 152 | 1 | 0.2 | 8.75 | 0.91 | N/S | N/S | 419 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-21 | 4.03 | 7.2 | 7 | N/S | N/S | N/S | 7 | 6 | 1110 | 146 | 1 | 0.1 | 9.15 | 1.1 | N/S | N/S | 387 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-22 | 3.14 | 7.2 | 6.7 | 4 | <2 | N/S | 5 | 4 | 1122 | 136 | 1 | 0.4 | 10.32 | 1.4 | N/S | N/S | 371 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-23 | 3.3 | 7.3 | 6.6 | <2 | <2 | <5 | <4 | <4 | 1114 | 124 | 2 | 0.2 | 11.73 | 1.4 | <0.005 | 5 | 353 | 0.6 | 400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-01-24 | 4.01 | 7.3 | 7.2 | 3 | <2 | N/S | <4 | <4 | 1052 | 100 | 2 | 0.4 | 11.78 | 1.37 | N/S | N/S | 348 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.004 | <0.05 | N/S | <0.01 | 0.007 | N/S | <0.005 | 0.011 | <0.001 | 0.02 | <0.03 | <0.001 | <0.03 | N/S | 85 | 37 | 365 | 2.9 | 3
2017-01-25 | 2.97 | 7.3 | 7.1 | 3 | <2 | N/S | <4 | <4 | 1130 | 136 | 2 | 0.6 | 12.06 | 1.65 | N/S | N/S | 361 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-26 | 2.67 | 7.3 | 6.8 | 3 | <2 | N/S | <4 | <4 | 1072 | 98 | 2 | 0.5 | 14.95 | 1.87 | N/S | N/S | 347 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-27 | 2.24 | 7.3 | 6.3 | N/S | N/S | N/S | 7 | 4 | 1138 | 138 | 2 | 0.1 | 15.78 | 2.06 | N/S | N/S | 349 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-28 | 2.64 | 7.2 | 7 | N/S | N/S | N/S | 7 | 5 | 1130 | 112 | 2 | 0.8 | 15.6 | 2.12 | N/S | N/S | 339 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-29 | 2.13 | 7.3 | 6 | 4 | <2 | N/S | 5 | 4 | 1160 | 164 | 2 | 0.1 | 16.41 | 2.11 | N/S | N/S | 347 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-01-30 | 2.24 | 7.3 | 7.5 | T/X | T/X | <5 | 5 | 4 | 1142 | 128 | 2 | 0.1 | 18.49 | 2.27 | <0.005 | 5 | 145 | 0.8 | 2300 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-01-31 | 2.23 | 7.3 | 7.2 | T/X | T/X | N/S | <4 | <4 | 1062 | 130 | 2 | 0.2 | 18.82 | 2.61 | N/S | N/S | 299 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.007 | 0.05 | N/S | <0.01 | 0.005 | N/S | <0.005 | 0.006 | <0.001 | 0.024 | <0.03 | <0.001 | 0.04 | N/S | 85 | 37 | 366 | 4.1 | 3
2017-02-01 | 2.23 | 7.4 | 6.7 | 6 | 3 | N/S | <4 | <4 | 1052 | 142 | 2 | <0.1 | 20.87 | 2.63 | N/S | N/S | 289 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-02 | 2.36 | 7.3 | 6.8 | 10 | 4 | N/S | 7 | 6 | 1152 | 166 | 2 | 0.2 | 18.57 | 2.67 | N/S | N/S | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-03 | 2.29 | 7.4 | 8.5 | N/S | N/S | N/S | 4 | 4 | 1293 | 226 | 3 | 0.6 | 16.24 | 2.76 | N/S | N/S | 371 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-04 | 1.99 | 7.3 | 7.2 | N/S | N/S | N/S | 4 | <4 | 1172 | 160 | 2 | 0.6 | 15.32 | 2.52 | N/S | N/S | 330 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-05 | 1.81 | 7.3 | 6.8 | 5 | 3 | N/S | <4 | <4 | 1124 | 154 | 2 | 0.3 | 16.83 | 2.37 | N/S | N/S | 313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-06 | 1.97 | 7.3 | 6.6 | T/X | T/X | <5 | 6 | 5 | 1093 | 128 | 2 | 0.3 | 18.21 | 2.82 | <0.005 | 5 | 313 | 1 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-02-07 | 3.69 | 7.4 | 5 | T/X | T/X | N/S | 9 | 8 | 1002 | 100 | 4 | 2.3 | 11.4 | 2.31 | N/S | N/S | 326 | N/S | N/S |  | 0.034 | <0.001 | <0.003 | 0.007 | 0.09 | <0.05 | <0.01 | 0.025 | N/S | <0.005 | <0.005 | <0.001 | 0.028 | <0.03 | <0.001 | <0.03 | N/S | 84 | 34 | 349 | T/X | 4
2017-02-08 | 3.33 | 7.1 | 6.3 | T/X | T/X | N/S | <4 | <4 | 1012 | 106 | 2 | 0.2 | 12.18 | 1.57 | N/S | N/S | 322 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-09 | 2.83 | 7.3 | 7.4 | T/X | T/X | N/S | 7 | 6 | 1118 | 146 | 3 | 0.7 | 12.06 | 1.85 | N/S | N/S | 368 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-10 | 2.37 | 7.3 | 6.2 | N/S | N/S | N/S | 22 | 18 | 1232 | 202 | 3 | 0.3 | 13.44 | 2.05 | N/S | N/S | 377 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-11 | 2.38 | 7.3 | 7.1 | N/S | N/S | N/S | 5 | 4 | 1221 | 168 | 3 | 0.8 | 14.78 | 2.1 | N/S | N/S | 379 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-12 | 2.34 | 7.3 | 5.8 | T/X | T/X | N/S | 7 | 5 | 1264 | 176 | 3 | 0.9 | 16.06 | 2.47 | N/S | N/S | 391 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-13 | 2.18 | 7.2 | 7.1 | T/X | T/X | <5 | 11 | 9 | 1166 | 128 | 2 | 0.5 | 18.2 | 2.54 | 0.005 | <5 | 373 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-14 | 2.13 | 7.3 | 7 | T/X | T/X | N/S | <4 | <4 | 1200 | 166 | 2 | 0.3 | 18.01 | 2.67 | N/S | N/S | 344 | N/S | 11000 | <0.02 | 0.033 | <0.001 | <0.003 | 0.006 | 0.05 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.008 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | <6 | 87 | 36 | 367 | 3.2 | 4
2017-02-15 | 2.14 | 7.3 | 7.6 | 3 | 3 | N/S | <4 | <4 | 1123 | 130 | 1 | 0.3 | 18.25 | 2.71 | N/S | N/S | 333 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-16 | 2.07 | 7.3 | 7 | 3 | <2 | N/S | <4 | <4 | 1127 | 132 | 2 | 0.3 | 19.84 | 2.64 | N/S | N/S | 339 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-17 | 2.04 | 7.3 | 7.2 | N/S | N/S | N/S | <4 | <4 | 1212 | 186 | 2 | 0.4 | 20.05 | 2.68 | N/S | N/S | 346 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-18 | 2.08 | 7.3 | 6 | N/S | N/S | N/S | <4 | <4 | 1191 | 182 | 3 | 0.9 | 19.46 | 2.82 | N/S | N/S | 340 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-19 | 2.04 | 7.3 | 5.6 | T/X | T/X | N/S | 5 | 5 | 1176 | 176 | 3 | 1.1 | 19.49 | 2.95 | N/S | N/S | 337 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-20 | 2.02 | 7.2 | 5.9 | 5 | 3 | <5 | <4 | <4 | 1172 | 156 | 2 | 0.7 | 20.58 | 2.92 | <0.005 | 6 | 332 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-21 | 2.06 | 7.4 | 5.8 | T/X | T/X | N/S | 4 | <4 | 1086 | 118 | 2 | 0.4 | 18.69 | 2.82 | N/S | N/S | 319 | N/S | 800 | <0.02 | 0.036 | 0.001 | <0.003 | 0.006 | 0.06 | N/S | <0.01 | 0.007 | N/S | <0.005 | <0.005 | <0.001 | 0.045 | <0.03 | <0.001 | <0.03 | <6 | 89 | 36 | 370 | 2.7 | 5
2017-02-22 | 1.99 | 7.3 | 6.8 | T/X | T/X | N/S | 5 | 4 | 1084 | 116 | 3 | 0.4 | 18.85 | 2.89 | N/S | N/S | 309 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-23 | 2.04 | 7.3 | 6.6 | T/X | T/X | N/S | 6 | 4 | 1120 | 166 | 2 | 0.3 | 19.11 | 2.93 | N/S | N/S | 327 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-24 | 2.57 | 7.2 | 8.1 | N/S | N/S | N/S | 39 | 34 | 1166 | 194 | 6 | 0.9 | 16.19 | 3.03 | N/S | N/S | 348 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-25 | 2.26 | 7.4 | 7.2 | N/S | N/S | N/S | 47 | 41 | 1172 | 192 | 5 | 0.7 | 15.59 | 2.87 | N/S | N/S | 345 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-26 | 2.19 | 7.2 | 8.3 | T/X | T/X | N/S | 36 | 31 | 1202 | 192 | 5 | 0.8 | 15.44 | 2.71 | N/S | N/S | 360 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-02-27 | 2.15 | 7.3 | 7.7 | 26 | 15 | <5 | 26 | 22 | 1206 | 162 | 7 | 2.9 | 12.2 | 3.03 | <0.005 | 10 | 366 | 1 | 14000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-02-28 | 2.51 | 7.2 | 7.3 | T/X | T/X | N/S | 5 | 4 | 1020 | 78 | 3 | 0.8 | 9.11 | 2.17 | N/S | N/S | 332 | N/S | N/S | <0.02 | 0.033 | 0.001 | <0.003 | 0.008 | 0.07 | N/S | <0.01 | 0.03 | N/S | <0.005 | 0.012 | <0.001 | 0.027 | <0.03 | <0.001 | <0.03 | N/S | 84 | 35 | 352 | 8.5 | 6
2017-03-01 | 4.46 | 7.2 | 9.2 | T/X | T/X | N/S | 7 | 6 | 700 | 82 | 2 | 0.1 | 6.54 | 1.08 | N/S | N/S | 225 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-02 | 4.47 | 7.2 | 8.7 | T/X | T/X | N/S | <4 | <4 | 800 | 90 | 2 | 0.8 | 6.99 | 0.83 | N/S | N/S | 238 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-03 | 3.26 | 7.3 | 8.7 | N/S | N/S | N/S | <4 | <4 | 938 | 114 | 2 | 0.9 | 9.6 | 1.02 | N/S | N/S | 280 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-04 | 3.1 | 7.3 | 7.5 | N/S | N/S | N/S | <4 | <4 | 924 | 116 | 3 | 1.8 | 11.51 | 1.29 | N/S | N/S | 250 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-05 | 3.11 | 7.2 | 8 | 4 | <2 | N/S | <4 | <4 | 982 | 116 | 5 | 3.6 | 11.84 | 1.74 | N/S | N/S | 270 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-06 | 2.34 | 7.2 | 6.1 | T/X | T/X | <5 | 6 | 4 | 1105 | 146 | 5 | 3.1 | 11.52 | 1.93 | <0.005 | 5 | 329 | 0.7 | 3900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-03-07 | 3.11 | 7.3 | 6 | 9 | 5 | N/S | 10 | 9 | 984 | 104 | 4 | 2.1 | 11.9 | 1.55 | N/S | N/S | 313 | N/S | N/S | <0.02 | 0.038 | 0.001 | <0.003 | 0.011 | 0.1 | <0.05 | <0.01 | 0.01 | N/S | <0.005 | 0.007 | <0.001 | 0.029 | <0.03 | <0.001 | <0.03 | N/S | 91 | 39 | 387 | 14 | 4
2017-03-08 | 3.1 | 7.2 | 6.5 | 8 | 3 | N/S | 5 | 4 | 1046 | 106 | 4 | 2.4 | 12.95 | 2.02 | N/S | N/S | 338 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-09 | 3.04 | 7.2 | 7.2 | 8 | 3 | N/S | 4 | <4 | 1068 | 88 | 4 | 2.3 | 13.86 | 2.12 | N/S | N/S | 335 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-10 | 3.15 | 7.2 | 6.5 | N/S | N/S | N/S | 29 | 24 | 1086 | 136 | 7 | 1.5 | 14.03 | 2.51 | N/S | N/S | 322 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-11 | 3.15 | 7.3 | 7.5 | N/S | N/S | N/S | 17 | 14 | 962 | 140 | 5 | 2.7 | 13.55 | 2.15 | N/S | N/S | 260 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-12 | 3.08 | 7.3 | 7.4 | 16 | 6 | N/S | 12 | 10 | 1033 | 138 | 8 | 6.1 | 11.81 | 2.49 | N/S | N/S | 287 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-13 | 1.92 | 7.1 | 6.4 | 10 | 4 | <5 | 7 | 6 | T/X | T/X | 4 | 1.3 | 16.78 | 2.28 | 0.006 | 5 | 369 | 0.9 | 8200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-03-14 | 2.14 | 7.2 | 7.3 | 7 | 3 | N/S | 7 | 6 | 1432 | 162 | 2 | 0.3 | 16.94 | 2.18 | N/S | N/S | 506 | N/S | N/S | <0.02 | 0.039 | <0.001 | <0.003 | 0.008 | 0.08 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.005 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | N/S | 104 | 41 | 431 | 7.1 | 3
2017-03-15 | 2.14 | 7.3 | 7.5 | 6 | 3 | N/S | 7 | 7 | 1550 | 206 | 2 | 0.2 | 16.94 | 2.26 | N/S | N/S | 554 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-16 | 2.77 | 7.2 | 7.7 | T/X | T/X | N/S | 7 | 6 | 1457 | 190 | 3 | 1.2 | 16.71 | 2.26 | N/S | N/S | 507 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-17 | 2.62 | 7.3 | 7 | N/S | N/S | N/S | 10 | 8 | 1334 | 134 | 4 | 1.3 | 17.11 | 2.6 | N/S | N/S | 442 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-18 | 2.35 | 7.3 | 6.8 | N/S | N/S | N/S | 7 | 6 | 1352 | 188 | 3 | 0.5 | 18.25 | 2.61 | N/S | N/S | 440 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-19 | 2.33 | 7.2 | 7 | 9 | 5 | N/S | 9 | 7 | 1186 | 154 | 3 | 0.4 | 17.77 | 2.76 | N/S | N/S | 355 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-20 | 3.8 | 7.1 | 5.8 | 7 | 3 | <5 | 7 | 6 | 928 | 122 | 2 | 0.2 | 11.93 | 1.7 | 0.008 | 7 | 314 | 0.6 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-03-21 | 4.08 | 7.2 | 7.5 | 4 | 3 | N/S | 5 | 4 | 908 | 116 | 1 | 0.1 | 10.6 | 1.21 | N/S | N/S | 294 | N/S | N/S | <0.02 | 0.029 | <0.001 | <0.003 | 0.004 | 0.05 | N/S | <0.01 | 0.005 | N/S | <0.005 | <0.005 | <0.001 | 0.018 | <0.03 | <0.001 | <0.03 | N/S | 79 | 35 | 343 | 23.3 | 3
2017-03-22 | 3.36 | 7.2 | 7.2 | 3 | <2 | N/S | <4 | <4 | 1162 | 177 | 2 | 0.1 | 12.95 | 1.56 | N/S | N/S | 352 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-23 | 3.34 | 7.2 | 7 | 4 | 2 | N/S | 4 | <4 | 1140 | 174 | 2 | 0.3 | 14.2 | 1.6 | N/S | N/S | 337 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-24 | 4.11 | 7.3 | 6.7 | N/S | N/S | N/S | 8 | 6 | 1002 | 114 | 2 | 0.4 | 12.3 | 1.55 | N/S | N/S | 314 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-25 | 4.17 | 7.1 | 7.4 | N/S | N/S | N/S | 8 | 7 | 950 | 124 | 2 | 0.2 | 10.96 | 1.34 | N/S | N/S | 310 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-26 | 4.15 | 7.4 | 8 | 7 | 3 | N/S | 6 | 5 | 874 | 122 | 1 | 0.2 | 10.2 | 1.14 | N/S | N/S | 270 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-27 | 4.13 | 7.2 | 8 | 6 | 3 | <5 | 7 | 5 | 956 | 124 | 2 | 0.2 | 10.77 | 1.26 | <0.005 | <5 | 282 | 0.5 | 2100 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-03-28 | 3.33 | 7.1 | 6.2 | 6 | 3 | N/S | 6 | 5 | 1094 | 176 | 1 | 0.2 | 11.79 | 1.44 | N/S | N/S | 319 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.008 | 0.07 | N/S | <0.01 | 0.009 | N/S | <0.005 | <0.005 | <0.001 | 0.02 | <0.03 | <0.001 | <0.03 | N/S | 95 | 41 | 405 | 2.7 | 4
2017-03-29 | 3.96 | 7.2 | 8.5 | 6 | 3 | N/S | 6 | 5 | 1083 | 170 | 1 | 0.2 | 11.83 | 1.31 | N/S | N/S | 316 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-30 | 3.97 | 7.4 | 7.4 | T/X | T/X | N/S | 5 | 4 | 628 | 74 | 1 | 0.1 | 7.91 | 0.97 | N/S | N/S | 181 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-03-31 | 4.21 | 7.4 | 6.9 | N/S | N/S | N/S | <4 | <4 | 736 | 130 | 1 | 0.1 | 7.49 | 0.83 | N/S | N/S | 201 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-01 | 4.3 | 7.5 | 7.6 | N/S | N/S | N/S | <4 | <4 | 900 | 152 | 1 | 0.1 | 10 | 0.91 | N/S | N/S | 244 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-02 | 4.3 | 7.3 | 7.4 | 3 | <2 | N/S | <4 | <4 | 822 | 136 | 1 | 0.2 | 11.15 | 1.08 | N/S | N/S | 245 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-03 | 3.85 | 7.4 | 5.5 | 3 | <2 | <5 | <4 | <4 | 956 | 148 | 1 | 0.6 | 10.88 | 1.23 | 0.005 | <5 | 261 | 0.5 | 8000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 6 | N/S | N/S | N/S | N/S | N/S
2017-04-04 | 3.55 | 7.4 | 7 | T/X | T/X | N/S | 7 | 6 | 982 | 158 | 1 | 0.4 | 11.99 | 1.51 | N/S | N/S | 273 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.004 | 0.09 | <0.05 | <0.01 | 0.02 | N/S | <0.005 | <0.005 | <0.001 | 0.024 | <0.03 | <0.001 | <0.03 | N/S | 89 | 40 | 387 | 0.6 | 5
2017-04-05 | 3.25 | 7.3 | 7 | 7 | 3 | N/S | 6 | 5 | 964 | 156 | <1 | 0.2 | 10.66 | 1.24 | N/S | N/S | 282 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-06 | 4.43 | 7.2 | 6.6 | T/X | T/X | N/S | 10 | 8 | 714 | 128 | 1 | 0.1 | 7.86 | 0.9 | N/S | N/S | 189 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-07 | 4.42 | 7.2 | 7.5 | N/S | N/S | N/S | 12 | 10 | 814 | 128 | 1 | 0.1 | 8.76 | 1 | N/S | N/S | 216 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-08 | 4.42 | 7.3 | 7.4 | N/S | N/S | N/S | 9 | 8 | 908 | 142 | 1 | 0.1 | 9.97 | 1.14 | N/S | N/S | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-09 | 4.38 | 7.3 | 6.2 | T/X | T/X | N/S | 13 | 11 | 954 | 148 | 1 | 0.3 | 9.81 | 1.21 | N/S | N/S | 264 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-10 | 4.33 | 7.3 | 6.6 | 7 | 3 | N/S | 4 | 4 | 968 | 162 | 1 | 0.4 | 9.64 | 1.05 | <0.005 | 6 | 268 | 0.6 | 2000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-04-11 | 4.32 | 7.3 | 6.1 | 5 | <2 | <5 | <4 | <4 | 874 | 118 | 1 | 0.1 | 9.63 | 0.89 | N/S | N/S | 247 | N/S | N/S | <0.02 | 0.035 | <0.001 | <0.003 | 0.006 | 0.07 | N/S | <0.01 | 0.008 | N/S | <0.005 | <0.005 | <0.001 | 0.018 | <0.03 | <0.001 | <0.03 | N/S | 85 | 39 | 372 | 4 | 4
2017-04-12 | 4.37 | 7.3 | 7 | 7 | 3 | N/S | 6 | 5 | 940 | 172 | 1 | 0.2 | 10.57 | 1.13 | N/S | N/S | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-13 | 3.85 | 7.6 | 5.7 | T/X | T/X | N/S | 4 | <4 | 960 | 128 | 1 | 0.2 | 10.26 | 1.25 | N/S | N/S | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-14 | 3.53 | 7.3 | 4.4 | N/S | N/S | N/S | <4 | <4 | 986 | 122 | 1 | 0.2 | 11.43 | 1.27 | N/S | N/S | 273 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-15 | 3.18 | 7.3 | 5.5 | N/S | N/S | N/S | <4 | <4 | 1046 | 130 | 1 | 0.3 | 11.55 | 1.45 | N/S | N/S | 291 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-16 | 4.08 | 7.4 | 6.2 | 16 | 6 | N/S | 14 | 11 | 924 | 120 | 2 | 0.5 | 10.54 | 1.5 | N/S | N/S | 258 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-17 | 3.43 | 7.3 | 5.1 | 11 | 7 | <5 | 14 | 10 | 956 | 156 | 2 | 0.2 | 10.75 | 1.49 | <0.005 | <5 | 236 | 0.7 | 79000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-04-18 | 3.16 | 7.4 | 6.4 | 9 | 5 | N/S | 8 | 6 | 1012 | 146 | 2 | 0.2 | 13.52 | 1.61 | N/S | N/S | 282 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.008 | 0.12 | N/S | <0.01 | 0.016 | N/S | <0.005 | <0.005 | <0.001 | 0.028 | <0.03 | <0.001 | <0.03 | N/S | 92 | 41 | 400 | 3.1 | 5
2017-04-19 | 3.13 | 7.3 | 6.6 | 7 | 4 | N/S | 7 | 5 | 1090 | 162 | 2 | 0.2 | 12.92 | 1.92 | N/S | N/S | 318 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-20 | 2.89 | 7.3 | 5.7 | 7 | 3 | N/S | 9 | 7 | 1123 | 194 | 1 | 0.2 | 13.75 | 1.87 | N/S | N/S | 315 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-21 | 2.44 | 7.3 | 6.7 | N/S | N/S | N/S | 7 | 6 | 1142 | 194 | 2 | 0.2 | 15.79 | 2.14 | N/S | N/S | 316 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-22 | 2.44 | 7.6 | 7.8 | N/S | N/S | N/S | 8 | 7 | 1088 | 182 | 3 | 0.7 | 15.67 | 2.5 | N/S | N/S | 295 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-23 | 2.43 | 7.5 | 7.5 | T/X | T/X | N/S | 9 | 7 | 1083 | 152 | 3 | 1.1 | 15.25 | 2.55 | N/S | N/S | 298 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-24 | 2.26 | 7.4 | 6.2 | 8 | 4 | <5 | 9 | 7 | 1150 | 182 | 2 | 0.5 | 16.4 | 2.42 | <0.005 | 10 | 313 | 1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-04-25 | 2.24 | 7.5 | 6.4 | 8 | 4 | N/S | 9 | 7 | 1131 | 166 | 2 | 0.4 | 16.83 | 2.56 | N/S | N/S | 313 | N/S | N/S | <0.02 | 0.039 | <0.001 | <0.003 | 0.008 | 0.15 | N/S | <0.01 | 0.031 | N/S | <0.005 | <0.005 | <0.001 | 0.034 | <0.03 | <0.001 | <0.03 | N/S | 103 | 42 | 431 | 4.8 | 6
2017-04-26 | 2.36 | 7.3 | 6.4 | 16 | 7 | N/S | 12 | 8 | 1126 | 162 | 5 | 1.8 | 14.61 | 2.96 | N/S | N/S | 314 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-27 | 3.07 | 7.4 | 6.4 | 11 | 8 | N/S | 12 | 10 | 1012 | 156 | 3 | 0.4 | 12.71 | 2.29 | N/S | N/S | 288 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-28 | 2.49 | 7.4 | 6.8 | N/S | N/S | N/S | 9 | 8 | 1020 | 160 | 3 | 0.2 | 14.79 | 2.18 | N/S | N/S | 293 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-29 | 2.81 | 7.4 | 6.5 | N/S | N/S | N/S | 13 | 10 | 880 | 160 | 3 | 0.3 | 14.03 | 2.13 | N/S | N/S | 239 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-04-30 | 4.45 | 7.2 | 6.5 | 10 | 5 | N/S | 13 | 10 | 524 | 120 | 2 | 0.2 | 7.09 | 0.89 | N/S | N/S | 119 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-01 | 4.46 | 7.3 | 7.1 | 6 | 3 | <5 | 10 | 7 | 516 | 94 | 1 | 0.1 | 6.25 | 0.67 | <0.005 | T/X | 100 | 0.3 | 1200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-05-02 | 4.47 | 7.4 | 6.8 | 6 | 3 | N/S | 9 | 7 | 620 | 124 | 2 | 0.1 | 7.63 | 0.74 | N/S | N/S | 118 | N/S | N/S | <0.02 | 0.025 | <0.001 | <0.003 | 0.006 | 0.13 | <0.05 | <0.01 | 0.005 | N/S | <0.005 | 0.005 | <0.001 | 0.017 | <0.03 | <0.001 | <0.03 | N/S | 63 | 28 | 273 | 4.7 | 5
2017-05-03 | 4.48 | 7.4 | 7.5 | 6 | 3 | N/S | 9 | 7 | 732 | 116 | 2 | 0.2 | 9.54 | 0.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-04 | 4.45 | 7.3 | 7.2 | 7 | 3 | N/S | 8 | 7 | 800 | 118 | 2 | 0.1 | 11.17 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-05 | 3.49 | 7.4 | 6.9 | N/S | N/S | N/S | 7 | 5 | 896 | 126 | 2 | 0.1 | 12.94 | 1.24 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-06 | 3.94 | 7.5 | 7.8 | N/S | N/S | N/S | 8 | 6 | 918 | 140 | 2 | 0.1 | 12.65 | 1.33 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-07 | 4.38 | 7.4 | 7.3 | 7 | 3 | N/S | 7 | 5 | 880 | 96 | 2 | 0.2 | 12.17 | 1.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-08 | 3.5 | 7.2 | 5.9 | 6 | 3 | 14 | 7 | 6 | 824 | 110 | 2 | 0.2 | 13.26 | 1.48 | <0.005 | 5 | N/S | 0.7 | 5000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-05-09 | 4.03 | 7.4 | 6.5 | 10 | 4 | N/S | 16 | 14 | 800 | 114 | 3 | 0.1 | 12.14 | 1.57 | N/S | N/S | 201 | N/S | N/S | <0.02 | 0.028 | <0.001 | <0.003 | 0.009 | 0.18 | N/S | <0.01 | 0.013 | N/S | <0.005 | <0.005 | <0.001 | 0.026 | <0.03 | <0.001 | <0.03 | N/S | 69 | 30 | 296 | 3.6 | 5
2017-05-10 | 3.84 | 7.3 | 7.7 | 4 | <2 | N/S | <4 | <4 | 744 | 110 | 2 | 0.1 | 11.31 | 1.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-11 | 4.41 | 7.2 | 7.1 | 7 | 2 | N/S | 8 | 7 | 634 | 102 | 3 | 0.1 | 9.75 | 1.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-12 | 4.32 | 7.4 | 6.9 | N/S | N/S | N/S | <4 | <4 | 636 | 64 | 2 | 0.1 | 10.26 | 1.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-13 | 3.74 | 7.4 | 7.1 | N/S | N/S | N/S | <4 | <4 | 820 | 86 | 2 | 0.2 | 12.34 | 1.34 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-14 | 3.97 | 7.3 | 6.5 | 4 | <2 | N/S | 5 | 4 | 872 | 160 | 2 | 0.2 | 13.89 | 1.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-15 | 3.67 | 7.4 | 6.1 | <2 | <2 | <5 | <4 | <4 | 910 | 178 | 1 | 0.2 | 13.17 | 1.47 | <0.005 | <5 | N/S | 0.6 | 900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-05-16 | 2.89 | 7.3 | 5.7 | 7 | 3 | N/S | 6 | 5 | 1049 | 246 | 2 | 0.4 | 13.74 | 2.09 | N/S | N/S | 226 | N/S | N/S | <0.02 | 0.04 | <0.001 | <0.003 | 0.004 | 0.09 | N/S | <0.01 | 0.017 | N/S | <0.005 | 0.019 | <0.001 | 0.029 | <0.03 | <0.001 | <0.03 | N/S | 95 | 40 | 404 | 2 | 5
2017-05-17 | 2.47 | 7.4 | 5.3 | 6 | 2 | N/S | 6 | 6 | 952 | 150 | 2 | 0.3 | 14.27 | 2.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-18 | 3.05 | 7.2 | 7.2 | T/X | T/X | N/S | 5 | 4 | 884 | 138 | 2 | 0.3 | 14.93 | 2.16 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-19 | 2.63 | 7.3 | 6.5 | N/S | N/S | N/S | 5 | 4 | 1020 | 238 | 2 | 0.2 | 17.44 | 2.27 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-20 | 2.8 | 7.3 | 6.4 | N/S | N/S | N/S | 6 | 4 | 952 | 198 | 2 | 0.2 | 16.92 | 2.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-21 | 3.52 | 7.4 | 7.2 | 5 | <2 | N/S | 6 | 4 | 860 | 146 | 2 | 0.2 | 14.76 | 1.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-22 | 3.13 | 7.2 | 6.8 | 5 | <2 | <5 | 5 | 5 | 1001 | 310 | 2 | 0.2 | 14.4 | 1.78 | <0.005 | 5 | N/S | 0.7 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-05-23 | 3.11 | 7.3 | 6.3 | 7 | 3 | N/S | 5 | 4 | 808 | 142 | 1 | 0.3 | 14.62 | 1.88 | N/S | N/S | 175 | N/S | N/S | <0.02 | 0.031 | <0.001 | <0.003 | 0.007 | 0.09 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.006 | <0.001 | 0.022 | <0.03 | <0.001 | <0.03 | N/S | 79 | 34 | 336 | 2.3 | 5
2017-05-24 | 4.22 | 7.3 | 6.8 | 7 | 3 | N/S | 8 | 7 | 668 | 108 | 2 | 0.1 | 10.39 | 1.35 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-25 | 4.06 | 7.3 | 6.7 | 6 | 3 | N/S | 7 | 6 | 834 | 176 | 2 | 0.1 | 10.96 | 1.28 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-26 | 3.24 | 7.3 | 6 | N/S | N/S | N/S | 7 | 5 | 868 | 174 | 2 | 0.1 | 13.73 | 1.64 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-27 | 3.78 | 7.3 | 6.3 | N/S | N/S | N/S | 7 | 5 | 842 | 148 | 2 | 0.1 | 12.54 | 1.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-28 | 3.12 | 7.4 | 5.4 | 5 | <2 | N/S | 6 | 4 | 914 | 174 | 2 | 0.1 | 15.2 | 1.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-29 | 3.08 | 7.4 | 6.1 | T/X | T/X | <5 | <4 | <4 | 990 | 168 | 2 | 0.4 | 15.23 | 2.28 | <0.005 | <5 | N/S | 0.7 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-05-30 | 2.46 | 7.4 | 5.7 | 7 | 4 | N/S | 8 | 6 | 1028 | 154 | 2 | 0.3 | 15.41 | 2.56 | N/S | N/S | 263 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.004 | 0.12 | N/S | <0.01 | 0.009 | N/S | <0.005 | <0.005 | <0.001 | 0.03 | <0.03 | <0.001 | <0.03 | <6 | 103 | 42 | 430 | 2.7 | 6
2017-05-31 | 2.3 | 7.4 | 5.9 | 3 | <2 | N/S | <4 | <4 | 1086 | 184 | 2 | 0.5 | 17.54 | 2.47 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-01 | 2.25 | 7.3 | 6.3 | 4 | <2 | N/S | <4 | <4 | 1138 | 180 | 3 | 0.3 | 19.53 | 2.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-02 | 2.18 | 7.4 | 6.1 | N/S | N/S | N/S | 5 | 4 | 1242 | 234 | 3 | 0.2 | 19.17 | 2.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-03 | 2.21 | 7.3 | 5.5 | N/S | N/S | N/S | 5 | 4 | 1255 | 182 | 2 | 0.4 | 17.82 | 2.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-04 | 2.16 | 7.4 | 5.5 | 7 | 3 | N/S | 6 | 4 | 1293 | 240 | 2 | 0.5 | 18.19 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-05 | 2.08 | 7.4 | 5 | 5 | 3 | <5 | 5 | 4 | 1228 | 186 | 2 | 0.4 | 19.49 | 2.75 | <0.005 | 5 | N/S | 1 | 1600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-06-06 | 2.04 | 7.5 | 6.4 | T/X | T/X | N/S | <4 | <4 | 1347 | 252 | 2 | 0.4 | 19.18 | 2.76 | N/S | N/S | 376 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.006 | 0.07 | <0.05 | <0.01 | 0.008 | N/S | <0.005 | 0.014 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | N/S | 117 | 44 | 474 | 2.7 | 5
2017-06-07 | 1.96 | 7.4 | 6.7 | T/X | T/X | N/S | 5 | 4 | 1414 | 308 | 2 | 0.3 | 19.73 | 2.83 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-08 | 1.95 | 7.4 | 5.3 | 5 | 2 | N/S | 4 | <4 | 1465 | 308 | 2 | 0.4 | 19.59 | 2.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-09 | 2.2 | 7.4 | 5.9 | N/S | N/S | N/S | 4 | <4 | 1420 | 312 | 2 | 0.4 | 18.74 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-10 | 2.1 | 7.4 | 4.7 | N/S | N/S | N/S | <4 | <4 | 1387 | 308 | 2 | 0.6 | 17.1 | 2.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-11 | 2.03 | 7.3 | 5 | 7 | 4 | N/S | <4 | <4 | 1406 | 314 | 3 | 0.8 | 17.3 | 2.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-12 | 1.93 | 7.4 | 5.6 | 6 | 4 | <5 | <4 | <4 | 1454 | 308 | 2 | 0.6 | 18.7 | 2.9 | <0.005 | 5 | N/S | 1 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-06-13 | 1.88 | 7.4 | 5.9 | 3 | 3 | N/S | 6 | 4 | 1346 | 226 | 2 | 0.5 | 18.98 | 2.8 | N/S | N/S | 379 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.008 | 0.07 | N/S | <0.01 | 0.011 | N/S | <0.005 | 0.012 | <0.001 | 0.035 | <0.03 | <0.001 | <0.03 | N/S | 117 | 43 | 468 | 6.5 | 6
2017-06-14 | 2.05 | 7.4 | 6.3 | 7 | 3 | N/S | 6 | 5 | 1355 | 340 | 7 | 0.5 | 18.19 | 2.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-15 | 1.97 | 7.3 | 6.6 | 7 | 3 | N/S | 6 | 5 | 1185 | 194 | 3 | 0.4 | 18.81 | 2.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-16 | 2.25 | 7.3 | 5.9 | N/S | N/S | N/S | 5 | 4 | 1245 | 240 | 3 | 0.3 | 18.77 | 2.75 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-17 | 2.17 | 7.2 | 7.2 | N/S | N/S | N/S | 7 | 6 | 1259 | 226 | 3 | 0.8 | 18.5 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-18 | 2.16 | 7.2 | 4.2 | 12 | 5 | N/S | 9 | 8 | 1236 | 224 | 5 | 1.9 | 16.71 | 3.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-19 | 2.04 | 7.2 | 5.1 | 9 | 4 | <5 | 9 | 7 | 1660 | 520 | 3 | 0.7 | 18.36 | 3.02 | <0.005 | <5 | N/S | 0.9 | 50000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-06-20 | 2.23 | 7.3 | 5.4 | T/X | T/X | N/S | <4 | <4 | 1431 | 320 | 2 | 0.4 | 18.77 | 2.59 | N/S | N/S | 415 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.007 | 0.05 | N/S | <0.01 | 0.008 | N/S | <0.005 | 0.008 | <0.001 | 0.03 | <0.03 | <0.001 | <0.03 | N/S | 106 | 38 | 423 | 2.9 | 5
2017-06-21 | 2.36 | 7.2 | 5.6 | 6 | 3 | N/S | 5 | 4 | 1142 | 184 | 3 | 0.3 | 17.9 | 2.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-22 | 1.97 | 7.2 | 5.6 | 6 | 3 | N/S | <4 | <4 | 1208 | 186 | 2 | 0.4 | 20.11 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-23 | 2.73 | 7.2 | 4.7 | N/S | N/S | N/S | <4 | <4 | 1074 | 226 | 2 | 0.7 | 14.4 | 1.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-24 | 3.04 | 7.2 | 5.2 | N/S | N/S | N/S | <4 | <4 | 1012 | 216 | 2 | 0.2 | 16.18 | 2.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-25 | 2.26 | 7.2 | 5.9 | 4 | 3 | N/S | <4 | <4 | 1254 | 280 | 3 | 0.8 | 16.81 | 2.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-26 | 1.74 | 7.3 | 4.7 | 8 | 3 | <5 | 7 | 6 | 1392 | 296 | 2 | 0.5 | 15.73 | 2.72 | <0.005 | 6 | N/S | 1 | 5900 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-06-27 | 1.85 | 7.3 | 5 | 6 | 3 | N/S | 6 | 5 | 1461 | 376 | 2 | 0.4 | 23.37 | 2.8 | N/S | N/S | 409 | N/S | N/S | <0.02 | 0.043 | <0.001 | 0.003 | 0.007 | 0.07 | N/S | <0.01 | 0.008 | N/S | <0.005 | 0.007 | <0.001 | 0.033 | <0.03 | <0.001 | <0.03 | N/S | 118 | 42 | 468 | 2.1 | 5
2017-06-28 | 2.13 | 7.4 | 5.5 | 11 | 5 | N/S | 7 | 6 | 1469 | 326 | 2 | 0.4 | 23.91 | 2.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-29 | 2.18 | 7.3 | 4.9 | 7 | 3 | N/S | 6 | 5 | 1424 | 448 | 2 | 0.4 | 19.44 | 2.65 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-06-30 | 2.46 | 7.3 | 4.6 | N/S | N/S | N/S | 7 | 6 | 1107 | 196 | 2 | 0.6 | 17.94 | 2.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-01 | 2.06 | 7.4 | 6.4 | N/S | N/S | N/S | 6 | 5 | 514 | 110 | 2 | 0.9 | 19.12 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-02 | 2.06 | 7.3 | 6.1 | 8 | 3 | N/S | 6 | 5 | 1204 | 204 | 2 | 0.3 | 21.71 | 2.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-03 | 2.02 | 7.4 | 5.7 | 6 | 3 | <5 | 5 | 4 | 1234 | 240 | 2 | 0.3 | 17.5 | 2.87 | <0.005 | T/X | N/S | 1 | 28000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-07-04 | 1.93 | 7.3 | 5.8 | 7 | 3 | N/S | 6 | 4 | 1286 | 228 | 2 | 0.6 | 13.78 | 2.95 | N/S | N/S | 348 | N/S | N/S | <0.02 | 0.037 | 0.001 | <0.003 | 0.008 | 0.08 | <0.05 | <0.01 | 0.014 | N/S | <0.005 | <0.005 | <0.001 | 0.035 | <0.03 | <0.001 | <0.03 | N/S | 113 | 42 | 455 | 6.9 | 5
2017-07-05 | 1.97 | 7.4 | 5.5 | 7 | 3 | N/S | 7 | 7 | 1326 | 296 | 2 | 0.5 | 20.01 | 2.95 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-06 | 1.9 | 7.3 | 6.6 | 7 | 3 | N/S | 7 | 5 | 1244 | 264 | 2 | 0.4 | 20.5 | 3.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-07 | 1.84 | 7.3 | 4.9 | N/S | N/S | N/S | <4 | <4 | 1552 | 466 | 2 | 0.4 | 18.21 | 3.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-08 | 1.87 | 7.4 | 4.9 | N/S | N/S | N/S | 6 | 5 | 1482 | 400 | 2 | 0.5 | 18.36 | 3.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-09 | 1.86 | 7.4 | 5.2 | T/X | T/X | N/S | 7 | 6 | 1508 | 432 | 2 | 0.4 | 21.34 | 3.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-10 | 2.46 | 7.4 | 4.2 | 9 | 4 | <5 | 10 | 8 | 1358 | 406 | 3 | 0.2 | 17.72 | 2.92 | <0.005 | <5 | N/S | 0.9 | 6500 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-07-11 | 2.41 | 7.3 | 5.2 | 8 | 4 | N/S | 9 | 7 | 1280 | 328 | 3 | 0.8 | 14.48 | 2.45 | N/S | N/S | 331 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.006 | 0.09 | N/S | <0.01 | 0.027 | N/S | <0.005 | 0.007 | <0.001 | 0.03 | <0.03 | <0.001 | <0.03 | N/S | 101 | 38 | 408 | 2.6 | 6
2017-07-12 | 2.04 | 7.3 | 4.7 | 7 | 4 | N/S | 7 | 5 | 1226 | 252 | 2 | 0.2 | 15.85 | 2.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-13 | 2.05 | 7.4 | 5.9 | 5 | 2 | N/S | 5 | <4 | 1213 | 242 | 2 | 0.3 | 18.22 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-14 | 2.07 | 7.2 | 5 | N/S | N/S | N/S | 6 | 4 | 830 | 228 | 3 | 0.5 | 17.55 | 2.78 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-15 | 2.04 | 7.4 | 6.7 | N/S | N/S | N/S | 5 | 4 | 1294 | 320 | 2 | 0.3 | 18.27 | 2.74 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-16 | 2.04 | 7.4 | 6.2 | 6 | 2 | N/S | 6 | 5 | 1255 | 340 | 3 | 0.5 | 17.31 | 2.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-17 | 1.91 | 7.4 | 6.5 | 6 | 2 | <5 | 6 | 5 | 1276 | 294 | 3 | 0.4 | 17.75 | 2.83 | <0.005 | <5 | N/S | 1.1 | 7700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-07-18 | 1.86 | 7.4 | 7.2 | 5 | <2 | N/S | 6 | 5 | 1240 | 258 | 2 | 0.4 | 19.52 | 2.97 | N/S | N/S | 333 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.006 | 0.07 | N/S | <0.01 | 0.011 | N/S | <0.005 | <0.005 | <0.001 | 0.037 | <0.03 | <0.001 | <0.03 | N/S | 105 | 37 | 418 | 1.5 | 4
2017-07-19 | 2.03 | 7.3 | 6.4 | 5 | <2 | N/S | 4 | 4 | 1216 | 320 | 2 | 0.3 | 17.69 | 2.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-20 | 3.21 | 7.2 | 6.8 | 6 | 2 | N/S | 6 | 5 | 890 | 272 | 1 | 0.3 | 9.92 | 1.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-21 | 3.14 | 7.2 | 6.5 | N/S | N/S | N/S | 10 | 7 | 976 | 250 | 2 | 0.3 | 10.28 | 1.32 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-22 | 4.42 | 7.2 | 6 | N/S | N/S | N/S | 4 | <4 | 664 | 146 | 1 | 0.1 | 7.28 | 0.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-23 | 3.63 | 7.2 | 8.2 | 6 | 3 | N/S | 7 | 6 | 446 | 124 | 1 | 0.1 | 6.87 | 0.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-24 | 4.5 | 7.2 | 8.8 | 7 | 3 | <5 | 13 | 11 | 814 | 210 | 1 | 0.1 | 7.08 | 1.1 | <0.005 | <5 | N/S | 0.4 | 11000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-07-25 | 3.33 | 7.2 | 8.6 | 5 | 2 | N/S | 5 | 4 | 1024 | 244 | 1 | 0.2 | 9.62 | 1.22 | N/S | N/S | 240 | N/S | N/S | <0.02 | 0.036 | 0.002 | <0.003 | 0.006 | 0.08 | N/S | <0.01 | 0.014 | N/S | <0.005 | 0.007 | <0.001 | 0.017 | <0.03 | <0.001 | <0.03 | N/S | 93 | 35 | 376 | 20.5 | 6
2017-07-26 | 2.47 | 7.4 | 9.8 | 7 | <2 | N/S | 12 | 9 | 1135 | 292 | 2 | 0.3 | 14.82 | 1.97 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-27 | 2.82 | 7.3 | 7.2 | 5 | <2 | N/S | 5 | 4 | 1013 | 176 | 1 | 0.2 | 13.91 | 1.81 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-28 | 2.89 | 7.3 | 8.3 | N/S | N/S | N/S | 20 | 14 | 1260 | 306 | 3 | 0.4 | 15.83 | 2.17 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-29 | 3.18 | 7.3 | 9.2 | N/S | N/S | N/S | 26 | 18 | 1336 | 364 | 3 | 0.4 | 16.73 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-30 | 2.52 | 7.2 | 6 | 8 | 3 | N/S | 11 | 8 | 1280 | 348 | 2 | 0.2 | 17.05 | 2.23 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-07-31 | 2.8 | 7.3 | 8 | 5 | 2 | <5 | 7 | 5 | 1104 | 222 | 3 | 0.2 | 17.45 | 2.02 | <0.005 | <5 | N/S | 0.8 | 5700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-08-01 | 2.52 | 7.3 | 9.3 | 8 | 3 | N/S | 9 | 7 | 1158 | 188 | 2 | 0.5 | 16.37 | 2.13 | N/S | N/S | 273 | N/S | N/S | <0.02 | 0.036 | <0.001 | <0.003 | 0.007 | 0.12 | <0.05 | <0.01 | 0.017 | N/S | <0.005 | 0.005 | <0.001 | 0.018 | <0.03 | <0.001 | <0.03 | N/S | 95 | 36 | 384 | 2.5 | 5
2017-08-02 | 2.13 | 7.3 | 6.4 | 4 | <2 | N/S | <4 | <4 | 1156 | 200 | 1 | 0.4 | 19.28 | 2.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-03 | 2.4 | 7.4 | 8.4 | 5 | 2 | N/S | 4 | <4 | 1062 | 214 | 2 | 0.4 | 19.2 | 2.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-04 | 3.22 | 7.2 | 6.1 | N/S | N/S | N/S | <4 | <4 | 836 | 146 | 1 | 0.2 | 14.03 | 1.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-05 | 2.82 | 7.3 | 6.3 | N/S | N/S | N/S | <4 | <4 | 954 | 160 | 1 | 0.4 | 16.53 | 1.71 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-06 | 2.08 | 7.4 | 6.3 | T/X | T/X | N/S | <4 | <4 | 1020 | 168 | 2 | 0.7 | 18.44 | 2.26 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-07 | 1.98 | 7.4 | 6.3 | 7 | 2 | <5 | <4 | <4 | 836 | 170 | 2 | 0.8 | 21.2 | 2.72 | <0.005 | <5 | N/S | 1 | 3600 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-08-08 | 1.95 | 7.4 | 6.3 | 6 | 2 | N/S | <4 | <4 | 1097 | 204 | 2 | 0.9 | 20.73 | 2.79 | N/S | N/S | 252 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.007 | 0.09 | N/S | <0.01 | 0.013 | N/S | <0.005 | 0.007 | <0.001 | 0.037 | <0.03 | <0.001 | <0.03 | N/S | 99 | 37 | 401 | 4.2 | 6
2017-08-09 | 1.88 | 7.4 | 6.3 | 8 | 2 | N/S | <4 | <4 | 1186 | 268 | 2 | 0.9 | 22.27 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-10 | 1.89 | 7.4 | 6.3 | 8 | 3 | N/S | 8 | 6 | 1168 | 252 | 2 | 0.9 | 21.21 | 2.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-11 | 1.87 | 7.4 | 6.3 | N/S | N/S | N/S | 8 | 6 | 1450 | 378 | 3 | 0.7 | 23.26 | 2.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-12 | 1.88 | 7.4 | 6.3 | N/S | N/S | N/S | 8 | 6 | 1518 | 388 | 2 | 0.8 | 23.55 | 2.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-13 | 1.85 | 7.4 | 6.3 | 8 | 3 | N/S | 5 | 4 | 1517 | 340 | 3 | 0.8 | 23.66 | 2.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-14 | 1.86 | 7.5 | 6.3 | 8 | <2 | <5 | 7 | 5 | 1439 | 300 | 2 | 0.6 | 22.29 | 2.71 | <0.005 | <5 | N/S | 1.6 | 4000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-08-15 | 1.85 | 7.4 | 6.3 | 4 | <2 | N/S | <4 | <4 | 1322 | 218 | 2 | 0.4 | 23.02 | 2.71 | N/S | N/S | 385 | N/S | N/S | <0.02 | 0.038 | <0.001 | <0.003 | 0.005 | 0.06 | N/S | <0.01 | 0.012 | N/S | <0.005 | 0.018 | <0.001 | 0.038 | <0.03 | <0.001 | <0.03 | N/S | 114 | 41 | 454 | 3.3 | 6
2017-08-16 | 1.94 | 7.2 | 6.3 | 5 | <2 | N/S | <4 | <4 | 1277 | 216 | 2 | 0.4 | 22.16 | 2.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-17 | 1.95 | 7.3 | 6.3 | 10 | 3 | N/S | 9 | 7 | 1422 | 312 | 3 | 0.5 | 22.08 | 2.72 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-18 | 1.83 | 7.3 | 6.3 | N/S | N/S | N/S | <4 | <4 | 1328 | 274 | 2 | 0.4 | 21.74 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-19 | 1.78 | 7.4 | 6.3 | N/S | N/S | N/S | <4 | <4 | 1326 | 254 | 2 | 0.5 | 22.95 | 2.86 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-20 | 1.81 | 7.4 | 6.3 | 7 | 2 | N/S | <4 | <4 | 1326 | 282 | 2 | 0.6 | 23.88 | 2.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-21 | 1.99 | 7.4 | 6.3 | 6 | 3 | <5 | <4 | <4 | 1198 | 260 | 2 | 0.3 | 20.73 | 2.74 | <0.005 | 5 | N/S | 1 | 31000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 6 | N/S | N/S | N/S | N/S | N/S
2017-08-22 | 2.7 | 7.2 | 6.3 | 5 | <2 | N/S | <4 | <4 | 956 | 180 | 1 | 0.3 | 18.16 | 2.19 | N/S | N/S | 247 | N/S | N/S | <0.02 | 0.028 | <0.001 | <0.003 | <0.004 | 0.05 | N/S | <0.01 | 0.008 | N/S | <0.005 | <0.005 | <0.001 | 0.021 | <0.03 | <0.001 | <0.03 | N/S | 86 | 32 | 348 | 3.8 | 5
2017-08-23 | 1.97 | 7.4 | 6.3 | 7 | 3 | N/S | 7 | 6 | 1052 | 206 | 3 | 0.4 | 18.71 | 2.63 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-24 | 1.83 | 7.4 | 6.3 | 8 | 3 | N/S | 7 | 5 | 1170 | 244 | 2 | 0.3 | 21.57 | 2.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-25 | 1.73 | 7.5 | 6.5 | N/S | N/S | N/S | 7 | 6 | 1182 | 250 | 2 | 0.3 | 23.36 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-26 | 1.8 | 7.2 | 5 | N/S | N/S | N/S | 9 | 7 | 1252 | 236 | 3 | 0.3 | 23.41 | 3.31 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-27 | 1.77 | 7.4 | 4.7 | 12 | 4 | N/S | 14 | 9 | 1341 | 340 | 3 | 0.4 | 22.66 | 3.2 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-28 | 1.94 | 7.3 | 5 | 12 | 5 | <5 | 10 | 8 | 1218 | 224 | 3 | 0.3 | 21.41 | 2.98 | <0.005 | <5 | N/S | 1.1 | 86000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-08-29 | 2.18 | 7.4 | 7 | 11 | 4 | N/S | 11 | 8 | 1130 | 220 | 2 | 0.2 | 18.41 | 2.86 | N/S | N/S | 316 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.009 | 0.13 | N/S | <0.01 | 0.014 | N/S | <0.005 | <0.005 | <0.001 | 0.039 | <0.03 | <0.001 | <0.03 | N/S | 102 | 36 | 404 | 3 | 5
2017-08-30 | 2.64 | 7.1 | 4.8 | 6 | 3 | N/S | 7 | 6 | 996 | 196 | 2 | 0.2 | 17.39 | 2.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-08-31 | 1.8 | 7.5 | 6 | 7 | 3 | N/S | 5 | 4 | 1066 | 178 | 2 | 0.3 | 21.09 | 2.62 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-01 | 1.73 | 7.4 | 5.1 | N/S | N/S | N/S | <4 | <4 | 1186 | 216 | 2 | 0.3 | 24.02 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-02 | 1.73 | 7.4 | 5.3 | N/S | N/S | N/S | 6 | 4 | 1158 | 198 | 2 | 0.3 | 25.01 | 3.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-03 | 1.67 | 7.4 | 5.2 | 6 | 2 | N/S | 6 | 4 | 1122 | 184 | 2 | 0.3 | 25.29 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-04 | 1.71 | 7.4 | 5.4 | T/X | T/X | <5 | 6 | 5 | 1118 | 204 | 2 | 0.3 | 24.97 | 3.55 | <0.005 | <5 | N/S | 1 | 46000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-05 | 1.67 | 7.4 | 5.5 | 9 | <2 | N/S | 10 | 7 | 1032 | 164 | 2 | 0.4 | 23.82 | 3.28 | N/S | N/S | 254 | N/S | N/S | <0.02 | 0.033 | <0.001 | <0.003 | 0.006 | 0.11 | <0.05 | <0.01 | 0.009 | N/S | <0.005 | <0.005 | <0.001 | 0.044 | <0.03 | <0.001 | <0.03 | <6 | 85 | 31 | 338 | 1.4 | 5
2017-09-06 | 1.64 | 7.4 | 5.3 | 3 | <2 | N/S | <4 | <4 | 968 | 104 | 2 | 0.3 | 24.86 | 3.37 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-07 | 1.64 | 7.3 | 5.8 | 3 | <2 | N/S | <4 | <4 | 1100 | 184 | 2 | 0.4 | 25.94 | 3.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-08 | 1.67 | 7.3 | 4.7 | N/S | N/S | N/S | 4 | <4 | 1272 | 268 | 2 | 0.4 | 26.54 | 3.58 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-09 | 1.72 | 7.1 | 4.6 | N/S | N/S | N/S | 4 | <4 | 1270 | 278 | 2 | 0.5 | 25.98 | 3.66 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-10 | 1.67 | 7.2 | 5.7 | 13 | 3 | N/S | 8 | 6 | 1365 | 306 | 2 | 0.5 | 24.23 | 3.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-11 | 1.64 | 7.1 | 4.7 | 7 | 3 | <5 | 5 | 4 | 1464 | 430 | 2 | 0.5 | 23.95 | 3.35 | <0.005 | <5 | N/S | 1.1 | 13000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-09-12 | 1.6 | 7.1 | 4.3 | 3 | <2 | N/S | <4 | <4 | 1718 | 478 | 2 | 0.5 | 22.89 | 3.17 | N/S | N/S | 480 | N/S | N/S | <0.02 | 0.045 | <0.001 | <0.003 | 0.006 | 0.09 | N/S | <0.01 | 0.033 | N/S | <0.005 | 0.012 | <0.001 | 0.029 | <0.03 | <0.001 | <0.03 | N/S | 127 | 43 | 494 | 11.9 | 4
2017-09-13 | 1.65 | 7.2 | 5.1 | 8 | 2 | N/S | 8 | 6 | 1752 | 536 | 2 | 0.4 | 23.69 | 3.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-14 | 1.65 | 7.2 | 4.2 | 5 | <2 | N/S | 6 | <4 | 1540 | 362 | 2 | 0.4 | 24.19 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-15 | 1.61 | 7.2 | 5.1 | N/S | N/S | N/S | 7 | 5 | 1724 | 466 | 3 | 0.3 | 24.4 | 3.67 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-16 | 1.68 | 7.2 | 4.4 | N/S | N/S | N/S | 7 | 5 | 1806 | 488 | 4 | 0.3 | 24.92 | 3.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-17 | 1.65 | 7.3 | 4.3 | T/X | T/X | N/S | 4 | <4 | 1912 | 422 | 3 | 0.4 | 23.68 | 3.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-18 | 1.61 | 7.3 | 4.2 | 4 | <2 | <5 | <4 | <4 | 1759 | 384 | 3 | 0.3 | 24.86 | 3.52 | <0.005 | <5 | N/S | 1.2 | 8700 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-09-19 | 1.78 | 7.3 | 4.1 | 8 | <2 | N/S | 5 | 4 | 1678 | 384 | 5 | 0.3 | 22.29 | 3.27 | N/S | N/S | 530 | N/S | N/S | <0.02 | 0.048 | <0.001 | <0.003 | 0.005 | 0.07 | N/S | <0.01 | 0.008 | N/S | <0.005 | <0.005 | <0.001 | 0.041 | <0.03 | <0.001 | <0.03 | N/S | 128 | 40 | 488 | 2 | 4
2017-09-20 | 1.66 | 7.3 | 6 | 3 | <2 | N/S | <4 | <4 | 1360 | 196 | 2 | 0.3 | 23.24 | 3.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-21 | 1.66 | 7.3 | 4 | 5 | <2 | N/S | 4 | <4 | 1424 | 246 | 2 | 0.3 | 22.85 | 3.4 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-22 | 1.67 | 7.4 | 4.5 | N/S | N/S | N/S | <4 | <4 | 1525 | 330 | 2 | 0.4 | 23.86 | 3.5 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-23 | 1.66 | 7.1 | 5 | N/S | N/S | N/S | <4 | <4 | 1428 | 268 | 3 | 0.3 | 24.99 | 3.54 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-24 | 1.7 | 7 | 4.8 | 5 | <2 | N/S | <4 | <4 | 1465 | 292 | 2 | 0.2 | 23.64 | 3.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-25 | 1.69 | 7 | 3.8 | 4 | <2 | <5 | <4 | <4 | 578 | 90 | 1 | 0.3 | 23.94 | 3.4 | <0.005 | 7 | N/S | 1.2 | 400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-09-26 | 1.64 | 7.1 | 4.3 | 5 | <2 | N/S | <4 | <4 | 1637 | 376 | 2 | 0.4 | 24.46 | 3.46 | N/S | N/S | 515 | N/S | N/S | <0.02 | 0.043 | <0.001 | <0.003 | 0.004 | 0.05 | N/S | <0.01 | 0.005 | N/S | <0.005 | 0.005 | <0.001 | 0.036 | <0.03 | <0.001 | <0.03 | N/S | 128 | 42 | 494 | 1.4 | 3
2017-09-27 | 1.59 | 7.2 | 4.6 | 6 | <2 | N/S | 5 | <4 | 1572 | 350 | 2 | 0.3 | 24.69 | 3.56 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-28 | 1.72 | 7.1 | 5 | 14 | 2 | N/S | 10 | 7 | 1243 | 160 | 4 | 1.3 | 21.74 | 3.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-29 | 1.66 | 7 | 4.2 | N/S | N/S | N/S | 6 | 5 | 1322 | 212 | 3 | 1.3 | 18.79 | 3.29 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-09-30 | 1.65 | 7.2 | 5.9 | N/S | N/S | N/S | <4 | <4 | 1518 | 322 | 2 | 0.5 | 18.93 | 2.85 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-01 | 1.62 | 7.3 | 4.7 | <2 | <2 | N/S | <4 | <4 | 1382 | 196 | 2 | 0.4 | 16.83 | 3.13 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-02 | 1.55 | 7.2 | 4.9 | 5 | <2 | <5 | <4 | <4 | 1362 | 234 | 1 | 0.3 | 23.72 | 3.22 | <0.005 | <5 | N/S | 1.2 | 1400 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-10-03 | 1.58 | 7.2 | 3.9 | 7 | <2 | N/S | 4 | <4 | 1254 | 180 | 2 | 0.3 | 23.75 | 3.61 | N/S | N/S | 375 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.005 | 0.09 | <0.05 | <0.01 | 0.021 | N/S | <0.005 | 0.009 | <0.001 | 0.043 | <0.03 | <0.001 | <0.03 | N/S | 108 | 36 | 421 | 1.4 | 4
2017-10-04 | 1.75 | 7.1 | 4.5 | 8 | <2 | N/S | 5 | 4 | 1251 | 226 | 2 | 0.4 | 25.79 | 3.45 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-05 | 1.64 | 7.3 | 4.4 | 7 | <2 | N/S | <4 | <4 | 1258 | 248 | 2 | 0.3 | 23.51 | 3.21 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-06 | 2.06 | 7 | 4.1 | N/S | N/S | N/S | 5 | <4 | 1324 | 278 | 2 | 0.3 | 24.12 | 2.99 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-07 | 2.01 | 7 | 3.7 | N/S | N/S | N/S | 5 | 4 | 1121 | 236 | 2 | 0.2 | 18.58 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-08 | 2.58 | 7.1 | 6.3 | 5 | <2 | N/S | 5 | <4 | 812 | 102 | 1 | 0.2 | 15.15 | 2.03 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-09 | 2.22 | 7.1 | 5 | 7 | <2 | <5 | 8 | 7 | 1124 | 174 | 2 | 0.4 | 17.72 | 2.33 | <0.005 | <5 | N/S | 0.9 | 7800 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-10-10 | 1.85 | 7.1 | 5.2 | T/X | T/X | N/S | 8 | 6 | 1116 | 184 | 2 | 0.2 | 15.51 | 2.74 | N/S | N/S | 310 | N/S | N/S | <0.02 | 0.034 | <0.001 | <0.003 | 0.007 | 0.1 | N/S | <0.01 | 0.005 | N/S | <0.005 | <0.005 | <0.001 | 0.036 | <0.03 | <0.001 | <0.03 | N/S | 92 | 31 | 359 | 4 | 4
2017-10-11 | 3.81 | 7.1 | 4.3 | T/X | T/X | N/S | 14 | 11 | 746 | 142 | 2 | <0.1 | 10.69 | 1.52 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-12 | 2.98 | 7.1 | 4.2 | 4 | <2 | N/S | <4 | <4 | 808 | 136 | 1 | 0.2 | 12.02 | 1.25 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-13 | 2.17 | 7.1 | 4.9 | N/S | N/S | N/S | 7 | 5 | 1073 | 146 | 2 | 0.1 | 19.15 | 2.05 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-14 | 3.29 | 7.3 | 4.3 | N/S | N/S | N/S | 11 | 8 | 756 | 134 | 2 | 0.1 | 12.19 | 1.57 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-15 | 4.25 | 7.1 | 4.6 | T/X | T/X | N/S | 8 | 6 | 522 | 88 | 1 | 0.1 | 5.98 | 0.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-16 | 4.25 | 7.1 | 4.4 | T/X | T/X | <5 | 4 | <4 | 690 | 88 | 1 | 0.1 | 8.14 | 0.7 | <0.005 | <5 | N/S | 0.4 | 340000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-10-17 | 4.22 | 7.2 | 4 | 7 | 2 | N/S | 7 | 6 | 736 | 132 | 2 | 0.1 | 9.82 | 0.96 | N/S | N/S | 179 | N/S | N/S | <0.02 | 0.029 | <0.001 | <0.003 | 0.007 | 0.14 | N/S | <0.01 | 0.005 | N/S | <0.005 | <0.005 | <0.001 | 0.02 | <0.03 | <0.001 | <0.03 | N/S | 75 | 28 | 301 | 4.1 | 5
2017-10-18 | 3.72 | 7 | 4.7 | 7 | 3 | N/S | 15 | 12 | 806 | 100 | 2 | 0.1 | 12.58 | 1.22 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-19 | 2.97 | 7.1 | 5.1 | 6 | <2 | N/S | 6 | 4 | 866 | 140 | 2 | <0.1 | 14.08 | 1.42 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-20 | 2.94 | 7.1 | 4.6 | N/S | N/S | N/S | 5 | 4 | 880 | 110 | 1 | <0.1 | 14.32 | 1.48 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-21 | 3.28 | 7.1 | 3.9 | N/S | N/S | N/S | 6 | 4 | 890 | 120 | 2 | 0.6 | 15.03 | 1.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-22 | 2.71 | 7.1 | 4.7 | 7 | 3 | N/S | 8 | 6 | 824 | 96 | 2 | <0.1 | 15.62 | 1.9 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-23 | 4.36 | 7.1 | 3.7 | 8 | 3 | <5 | 11 | 8 | 640 | 102 | 2 | 0.1 | 12.8 | 1.43 | <0.005 | <5 | N/S | 0.6 | 53000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-10-24 | 4.34 | 6.9 | 4.3 | 7 | 3 | N/S | 11 | 8 | 572 | 100 | 1 | 0.1 | 9.26 | 1.06 | N/S | N/S | 102 | N/S | N/S | <0.02 | 0.022 | <0.001 | <0.003 | 0.006 | 0.17 | N/S | <0.01 | 0.006 | N/S | <0.005 | <0.005 | <0.001 | 0.021 | <0.03 | <0.001 | <0.03 | N/S | 59 | 24 | 243 | 2.1 | 5
2017-10-25 | 4.36 | 7.2 | 4.8 | 6 | 3 | N/S | 8 | 6 | 526 | 102 | 1 | 0.1 | 8.28 | 0.91 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-26 | 2.54 | 7.1 | 4.3 | 7 | 3 | N/S | 8 | 6 | 652 | 134 | 1 | 0.1 | 13.29 | 1.36 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-27 | 2.57 | 7.1 | 4.7 | N/S | N/S | N/S | 9 | 7 | 732 | 114 | 2 | <0.1 | 14.8 | 1.61 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-28 | 2.67 | 7.1 | 4.3 | N/S | N/S | N/S | 13 | 10 | 762 | 96 | 2 | 0.1 | 16.37 | 1.69 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-29 | 3.12 | 7.1 | 3.5 | 12 | 4 | N/S | 12 | 9 | 742 | 98 | 2 | 0.8 | 15.21 | 1.68 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-10-30 | 2.88 | 7 | 3.7 | 6 | 4 | <5 | 10 | 7 | 736 | 128 | 1 | 0.2 | 15.78 | 1.63 | 0.005 | <5 | N/S | 0.7 | 53000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-10-31 | 2.59 | 7 | 3.8 | 9 | 5 | N/S | 13 | 9 | 950 | 126 | 3 | 0.3 | 19.76 | 2.41 | N/S | N/S | 232 | N/S | N/S | <0.02 | 0.033 | <0.001 | <0.003 | 0.009 | 0.18 | N/S | <0.01 | 0.014 | N/S | <0.005 | <0.005 | <0.001 | 0.034 | <0.03 | <0.001 | <0.03 | N/S | 95 | 35 | 382 | 0.6 | 6
2017-11-01 | 2.22 | 7.2 | 3.8 | T/X | T/X | N/S | 17 | 13 | 1096 | 226 | 3 | 0.2 | 20.43 | 2.59 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-02 | 2.6 | 7 | 3.6 | 10 | 6 | N/S | 14 | 11 | 984 | 150 | 3 | 0.1 | 18.33 | 2.18 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-03 | 2.36 | 7.2 | 3.6 | N/S | N/S | N/S | 11 | 8 | 1041 | 176 | 3 | 0.1 | 18.16 | 2.12 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-04 | 2.31 | 7.2 | 4.2 | N/S | N/S | N/S | 16 | 12 | 884 | 144 | 3 | 0.1 | 16.95 | 2.19 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-05 | 2.77 | 7.1 | 5 | 16 | 8 | N/S | 18 | 13 | 912 | 134 | 3 | 0.2 | 16.01 | 1.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-06 | 2.64 | 7.1 | 3.6 | T/X | T/X | <5 | 129 | 101 | 1078 | 216 | 14 | 0.2 | 15.32 | 4.24 | 0.005 | 6 | N/S | 0.8 | 39000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-11-07 | 2.24 | 7.2 | 3.5 | 17 | 6 | N/S | 28 | 21 | 1070 | 156 | 5 | 0.1 | 17.81 | 2.61 | N/S | N/S | 287 | N/S | N/S | <0.02 | 0.036 | <0.001 | <0.003 | 0.014 | 0.23 | 0.05 | <0.01 | 0.022 | N/S | <0.005 | 0.009 | <0.001 | 0.038 | <0.03 | <0.001 | <0.03 | N/S | 95 | 37 | 391 | 5.9 | 7
2017-11-08 | 2.1 | 7.1 | 4 | 21 | 6 | N/S | 31 | 26 | 1080 | 270 | 5 | 0.1 | 18.72 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-09 | 1.89 | 7.2 | 4.3 | 18 | 7 | N/S | 30 | 25 | 1080 | 158 | 5 | 0.1 | 20.3 | 2.94 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-10 | 1.81 | 7.2 | 4.3 | N/S | N/S | N/S | 9 | 8 | 952 | 104 | 3 | 0.1 | 21.46 | 2.73 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-11 | 1.89 | 7.1 | 4 | N/S | N/S | N/S | 10 | 8 | 892 | 98 | 3 | 0.4 | 21.19 | 2.7 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-12 | 1.99 | 7.2 | 4.1 | 8 | 4 | N/S | 5 | 5 | 918 | 104 | 2 | 0.2 | 20.89 | 2.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-13 | 1.81 | 7.2 | 3.7 | 8 | 3 | <5 | 5 | 4 | 882 | 112 | 2 | 0.1 | 19.36 | 2.45 | <0.005 | <5 | N/S | 0.9 | 7200 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-11-14 | 1.78 | 7.2 | 3.9 | 5 | 2 | N/S | 4 | <4 | 1062 | 178 | 2 | 0.1 | 22.44 | 2.61 | N/S | N/S | 290 | N/S | N/S | <0.02 | 0.037 | <0.001 | <0.003 | 0.005 | 0.07 | N/S | <0.01 | 0.012 | N/S | <0.005 | <0.005 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | N/S | 108 | 38 | 430 | 1.2 | 6
2017-11-15 | 2.24 | 7.3 | 3.7 | 10 | 5 | N/S | 13 | 10 | 990 | 164 | 3 | 0.1 | 20.08 | 2.49 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-16 | 2.55 | 7.3 | 3.8 | T/X | T/X | N/S | 4 | <4 | 934 | 142 | 2 | 0.1 | 16.44 | 2.04 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-17 | 2.17 | 7.1 | 4.2 | N/S | N/S | N/S | 23 | 18 | 864 | 128 | 5 | 0.4 | 16.66 | 2.43 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-18 | 3.9 | 7.1 | 5.8 | N/S | N/S | N/S | 23 | 17 | 606 | 104 | 4 | <0.1 | 9.14 | 1.51 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-19 | 4.4 | 7.1 | 4.4 | 9 | 5 | N/S | 14 | 11 | 620 | 128 | 3 | 0.1 | 8.1 | 0.87 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-20 | 3.2 | 7 | 4.5 | 6 | 3 | <5 | 8 | 6 | 762 | 102 | 2 | 0.1 | 10.69 | 1.02 | <0.005 | <5 | N/S | 0.5 | 10000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-11-21 | 2.6 | 7.1 | 4.3 | 2 | <2 | N/S | <4 | <4 | 894 | 98 | 2 | 0.1 | 14.72 | 1.5 | N/S | N/S | 254 | N/S | N/S | <0.02 | 0.033 | <0.001 | <0.003 | 0.006 | 0.06 | N/S | <0.01 | 0.006 | N/S | <0.005 | 0.005 | <0.001 | 0.021 | <0.03 | <0.001 | <0.03 | N/S | 97 | 38 | 401 | 3 | 5
2017-11-22 | 2.63 | 7.1 | 4.3 | 6 | 4 | N/S | 9 | 7 | 1067 | 254 | 2 | 0.1 | 16.91 | 1.93 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-23 | 3.3 | 7.2 | 4.3 | 12 | 5 | N/S | 7 | 5 | 918 | 122 | 5 | 2.5 | 13.05 | 1.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-24 | 2.6 | 7.2 | 3.7 | N/S | N/S | N/S | <4 | <4 | 968 | 100 | 3 | 1.6 | 13.21 | 1.98 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-25 | 2.66 | 7.2 | 3.9 | N/S | N/S | N/S | <4 | <4 | 922 | 102 | 2 | 0.1 | 16.3 | 1.96 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-26 | 2.64 | 7.2 | 4 | 4 | 4 | N/S | <4 | <4 | 992 | 106 | 2 | 0.7 | 18.22 | 2.3 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-27 | 2.37 | 7.1 | 3.7 | 5 | 3 | <5 | <4 | <4 | 1090 | 116 | 3 | 1.5 | 16.3 | 2.65 | <0.005 | <5 | N/S | 0.9 | 25000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-11-28 | 1.94 | 7.2 | 3.8 | 8 | 3 | N/S | 6 | 5 | 658 | 80 | 3 | 0.3 | 17.32 | 2.52 | N/S | N/S | 318 | N/S | N/S | <0.02 | 0.039 | <0.001 | <0.003 | 0.004 | 0.09 | N/S | <0.01 | 0.013 | N/S | <0.005 | <0.005 | <0.001 | 0.052 | <0.03 | <0.001 | <0.03 | N/S | 104 | 38 | 419 | 1.5 | 5
2017-11-29 | 1.79 | 7.1 | 4.1 | 4 | <2 | N/S | <4 | <4 | 1063 | 144 | 2 | 0.2 | 21.28 | 2.6 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-11-30 | 1.87 | 7.2 | 3.9 | 8 | 3 | N/S | 9 | 7 | 1058 | 146 | 3 | 0.1 | 24.07 | 2.8 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-01 | 1.78 | 7.1 | 4 | N/S | N/S | N/S | 6 | 5 | 1000 | 124 | 2 | 0.1 | 23.14 | 2.81 | N/S | N/S | 244 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-02 | 1.89 | 7.3 | 4 | N/S | N/S | N/S | 4 | <4 | 946 | 112 | 3 | 0.3 | 23.05 | 2.89 | N/S | N/S | 221 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-03 | 1.87 | 7.1 | 3.9 | T/X | T/X | N/S | 5 | 4 | 912 | 116 | 3 | 0.4 | 21.99 | 2.92 | N/S | N/S | 194 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-04 | 1.9 | 7.1 | 3.8 | 12 | 7 | <5 | 7 | 6 | 898 | 134 | 3 | 0.6 | 19.2 | 2.72 | <0.005 | 13 | 191 | 1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-12-05 | 1.76 | 7.1 | 3.8 | 15 | 6 | N/S | 10 | 8 | 886 | 124 | 3 | 0.2 | 16.37 | 2.49 | N/S | N/S | 187 | N/S | 77000 | <0.02 | 0.029 | <0.001 | <0.003 | 0.008 | 0.11 | <0.05 | <0.01 | 0.012 | N/S | <0.005 | <0.005 | <0.001 | 0.04 | <0.03 | <0.001 | <0.03 | N/S | 75 | 29 | 308 | 1.3 | 7
2017-12-06 | 1.75 | 7.2 | 4.3 | T/X | T/X | N/S | 4 | <4 | 880 | 118 | 2 | 0.1 | 19.21 | 2.54 | N/S | N/S | 178 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-07 | 1.77 | 7.2 | 4.4 | 10 | 4 | N/S | 9 | 8 | 1014 | 144 | 2 | 0.1 | 21.89 | 2.62 | N/S | N/S | 246 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-08 | 1.76 | 7.2 | 4.4 | N/S | N/S | N/S | <4 | <4 | 1118 | 180 | 2 | 0.1 | 23.09 | 2.67 | N/S | N/S | 307 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-09 | 1.86 | 7.2 | 4.3 | N/S | N/S | N/S | 5 | 4 | 1140 | 168 | 2 | 0.2 | 22.25 | 2.76 | N/S | N/S | 318 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-10 | 1.86 | 7.2 | 4.2 | 11 | 4 | N/S | 7 | 6 | 1108 | 170 | 3 | 0.5 | 21.21 | 2.73 | N/S | N/S | 313 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-11 | 1.74 | 7.2 | 4 | 6 | 3 | <5 | 5 | 5 | 1138 | 146 | 2 | 0.2 | 19.18 | 2.65 | 0.006 | 10 | 321 | 1.1 | 27000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | <6 | N/S | N/S | N/S | N/S | N/S
2017-12-12 | 1.67 | 7.2 | 4.4 | 16 | 6 | N/S | 12 | 10 | 1146 | 116 | 3 | 0.3 | 18.96 | 2.76 | N/S | N/S | 341 | N/S | N/S | <0.02 | 0.032 | <0.001 | <0.003 | 0.008 | 0.11 | N/S | <0.01 | 0.018 | N/S | <0.005 | <0.005 | <0.001 | 0.036 | <0.03 | <0.001 | <0.03 | N/S | 95 | 34 | 376 | 2.5 | 6
2017-12-13 | 1.8 | 7.2 | 4 | T/X | 18 | N/S | 61 | 51 | 1226 | 202 | 13 | 0.2 | 18.77 | 4.37 | N/S | N/S | 256 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-14 | 1.84 | 7.3 | 4.1 | T/X | 7 | N/S | 29 | 25 | 1206 | 172 | 10 | 0.5 | 17.85 | 3.73 | N/S | N/S | 343 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-15 | 1.7 | 7.3 | 4.2 | N/S | N/S | N/S | 4 | <4 | 1120 | 112 | 2 | 0.2 | 17.97 | 2.67 | N/S | N/S | 316 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-16 | 1.78 | 7.2 | 4.3 | N/S | N/S | N/S | 23 | 19 | 1122 | 142 | 4 | 0.8 | 18.73 | 3.01 | N/S | N/S | 315 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-17 | 1.75 | 7.2 | 3.9 | 20 | 8 | N/S | 9 | 7 | 1052 | 118 | 5 | 1.8 | 17.87 | 3.18 | N/S | N/S | 277 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-18 | 1.7 | 7.2 | 3.6 | T/X | T/X | <5 | 12 | 10 | 1032 | 120 | 6 | 2.4 | 19.43 | 3.52 | <0.005 | <5 | 258 | 1.1 | 150000 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | 10 | N/S | N/S | N/S | N/S | N/S
2017-12-19 | 1.68 | 7.1 | 3.5 | 18 | 8 | N/S | 8 | 7 | 1124 | 142 | 6 | 2.2 | 19.71 | 3.16 | N/S | N/S | 310 | N/S | N/S | <0.02 | 0.03 | <0.001 | <0.003 | 0.009 | 0.08 | N/S | <0.01 | 0.024 | N/S | <0.005 | <0.005 | <0.001 | 0.041 | <0.03 | <0.001 | <0.03 | N/S | 88 | 30 | 345 | 3 | 7
2017-12-20 | 1.68 | 7.1 | 4 | 19 | 7 | N/S | 9 | 8 | 1086 | 154 | 4 | 1.4 | 18.49 | 2.65 | N/S | N/S | 286 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-21 | 1.68 | 7.2 | 3.8 | 15 | 5 | N/S | 5 | 4 | 1028 | 138 | 4 | 1.2 | 18.27 | 2.56 | N/S | N/S | 276 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-22 | 1.71 | 7.1 | 4 | N/S | N/S | N/S | 8 | 7 | 946 | 100 | 4 | 1.8 | 18.12 | 2.91 | N/S | N/S | 241 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-23 | 1.78 | 7.2 | 4 | N/S | N/S | N/S | 10 | 10 | 870 | 98 | 6 | 3.8 | 15.09 | 3.08 | N/S | N/S | 199 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-24 | 1.75 | 7.2 | 3.9 | T/X | T/X | N/S | 16 | 15 | 810 | 108 | 10 | 4.6 | 11.69 | 3.54 | N/S | N/S | 172 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-25 | 1.69 | 7.2 | 4.1 | 23 | 8 | <5 | 12 | 10 | 902 | 118 | 9 | 5.3 | 12.72 | 3.64 | <0.005 | <5 | 209 | 1.1 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-26 | 1.68 | 7.1 | 4.4 | 16 | 11 | N/S | 17 | 15 | 866 | 108 | 9 | 4.5 | 15.83 | 3.86 | N/S | N/S | 193 | N/S | 11000 | <0.02 | 0.026 | <0.001 | <0.003 | 0.011 | 0.13 | N/S | <0.01 | 0.026 | N/S | <0.005 | 0.006 | 0.001 | 0.036 | <0.03 | <0.001 | <0.03 | 10 | 76 | 28 | 304 | 1.8 | 11
2017-12-27 | 1.66 | 7.2 | 4.3 | 21 | 10 | N/S | 11 | 9 | 886 | 114 | 6 | 2.6 | 16.95 | 3.64 | N/S | N/S | 197 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-28 | 1.63 | 7.1 | 3.9 | 15 | 7 | N/S | 16 | 14 | 850 | 76 | 4 | 1.2 | 15.09 | 3.15 | N/S | N/S | 203 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-29 | 1.63 | 7.1 | 4.3 | N/S | N/S | N/S | 79 | 66 | 934 | 144 | 10 | 1.7 | 13.83 | 3.9 | N/S | N/S | 193 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-30 | 1.72 | 7.1 | 4.3 | N/S | N/S | N/S | 27 | 24 | 906 | 102 | 6 | 1.9 | 14.95 | 3.13 | N/S | N/S | 206 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
2017-12-31 | 1.73 | 7.1 | 4.5 | T/X | T/X | N/S | 15 | 14 | 924 | 98 | 9 | 2.2 | 16.94 | 3.41 | N/S | N/S | 217 | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S | N/S
PQL |  |  |  | 2 | 2 | 5 | 4 | 4 | 25 |  | 1 | 0.1 | 0.15 | 0.1 | 0.005 | 5 | 5 | 0.1 | 10 | 0.02 | 0.002 | 0.001 | 0.003 | 0.004 | 0.05 | 0.05 | 0.01 | 0.001 |  | 0.005 | 0.005 | 0.001 | 0.005 | 0.03 | 0.001 | 0.03 | 6 | 1 | 1 |  | 0.5 | 1
Observations | 365 | 365 | 365 | 211 | 213 | 52 | 365 | 365 | 364 | 364 | 365 | 365 | 365 | 365 | 52 | 49 | 183 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 12 | 52 | 52 | 0 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 52
Minimum | 1.55 | 6.9 | 3.5 | <2 | <2 | <5 | <4 | <4 | 446 | 64 | <1 | <0.1 | 5.98 | 0.67 | <0.005 | <5 | 100 | 0.3 | 400 | <0.02 | 0.022 | <0.001 | <0.003 | <0.004 | <0.05 | <0.05 | <0.01 | 0.005 |  | <0.005 | <0.005 | <0.001 | 0.017 | <0.03 | <0.001 | <0.03 | <6 | 59 | 24 | 243 | 0.6 | 3
Mean | 2.57 | 7.3 | 5.8 | <7 | <3 | <5 | <8 | <7 | 1081 | 186 | <3 | <0.5 | 16.7 | 2.33 | <0.005 | <6 | 304 | 0.9 | 25108 | <0.02 | 0.035 | <0.001 | <0.003 | <0.007 | <0.09 | <0.05 | <0.01 | 0.013 |  | <0.005 | <0.007 | <0.001 | 0.031 | <0.03 | <0.001 | <0.03 | <6 | 95 | 36 | 386 | 4.3 | 5
Maximum | 4.72 | 7.6 | 9.8 | 26 | 18 | 14 | 129 | 101 | 1912 | 536 | 14 | 6.1 | 26.54 | 4.37 | 0.008 | 13 | 554 | 1.6 | 340000 | <0.02 | 0.048 | 0.002 | 0.003 | 0.014 | 0.23 | 0.05 | <0.01 | 0.033 |  | <0.005 | 0.019 | 0.001 | 0.052 | <0.03 | <0.001 | 0.04 | 10 | 128 | 44 | 494 | 23.3 | 11
Std Dev | 0.86 | 0.1 | 1.4 | 4 | 2 | 1 | 10 | 8 | 241 | 86 | 2 | 0.7 | 4.67 | 0.77 | 0 | 2 | 79 | 0.2 | 52709 | 0 | 0.005 | 0 | 0 | 0.002 | 0.04 | 0 | 0 | 0.008 |  | 0 | 0.003 | 0 | 0.008 | 0 | 0 | 0 | 1 | 16 | 5 | 57 | 4.4 | 1
%>400=100
JANUARY 2, 2017 Phenol, T/X: The sample arrived at the lab chemically unpreserved.
JANUARY 15, 2017 NH3_N, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
JANUARY 9, 17, 30, 31, 2017 BOD5, CBOD5, T/X: Batch LCS failure.
FEBRUARY 5, 23, 26, 2017 NO2+NO3-N, : Sample MS recovery failed, but LCS passed.
FEBRUARY 6, 7, 8, 9, 12, 13, 14, 19, 21, 22, 23, 28, 2017 BOD5, CBOD5, T/X: Batch LCS failure.
FEBRUARY 7, 2017 LL Hg, T/X: Field Blank failure.
FEBRUARY 26, 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
FEBRUARY 24-27, 2017:The samples were heavy due to rain and road salt.
MARCH 1, 2, 6, 16, 2017 BOD5, CBOD5, T/X: Batch LCS failure.
MARCH 5, 2017 NH3_N, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
MARCH 7, 2017 TOT PHOS: Sample MS recovery failed, but LCS passed.
MARCH 13, 2017 TS, VTS; T/X: Insufficient sample volume for analysis .
MARCH 19, 2017 NH3_N: Sample MS recovery failed, but LCS passed.
MARCH 30, 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
APRIL 2, 16, 19, 29, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
APRIL 4, 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
APRIL 6, 9, 13, 23, 2017 BOD5, CBOD5, T/X: LCS failure.
APRIL 20, 2017 TKN: Sample MS recovery failed, but LCS passed.
MAY 1, Phenol T/X: LCS failure.
MAY 10, 21, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
MAY 15, 2017 TKN: Sample MS recovery failed, but LCS passed.
MAY 18, 29, , 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
JUNE 3, 2017 NH3_N: Sample MS recovery failed, but LCS passed.
JUNE 3, 14, 2017 NO2+NO3-N: Sample MS recovery failed, but LCS passed.
JUNE 6, 7, 2017 BOD5, CBOD5, T/X: LCS failure.
JUNE 8, 2017, TKN and TOT PHOS: Sample MS recovery failed, but LCS passed.
JUNE 20, 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
JULY 1, 16, 20, 29, 2017 NH3_N, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
JULY 3, 2017 Phenol, T/X: The sample was not thermally preserved.
JULY 5, 2017, TOT PHOS: Expired Molybdate(exp. 7/9/17) was used to run batch on 7/10/17.
JULY 9, 2017 BOD5, CBOD5, T/X: LCS failure.
AUGUST 6, 2017 BOD5, CBOD5, T/X: LCS failure.
AUGUST 13, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
AUGUST 22, 2017 CL: Two blanks were used for CL correction factor instead of three.
SEPTEMBER 4, 2017 BOD5, CBOD5, T/X: pH not adjusted as required by the method.
SEPTEMBER 13, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
SEPTEMBER 17, 2017 BOD5, CBOD5, T/X: Dilution water blank failure.
SEPTEMBER 23, 2017, TKN and TOT PHOS,T/X: Technician error.
OCTOBER 10, 11, 15, 16, 2017 BOD5, CBOD5, T/X: LCS failure.
OCTOBER 15, 2017 NH3_N: Sample MS recovery failed, but LCS passed.
OCTOBER 18, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
NOVEMBER 6, 2017: SS were high because the polishing tank out of service for a month.
NOVEMBER 1, 6, 16, 2017 BOD5, CBOD5, T/X: LCS failure.
NOVEMBER 15, 2017, TKN, NO2+NO3-N, TOT PHOS: Sample MS recovery failed, but LCS passed.
NOVEMBER 16, 17, 20, 2017 NH3_N, NO2+NO3-N: Sample MS recovery failed, but LCS passed.
DECEMBER 3, 6, 18, 24, 31, 2017 BOD5, CBOD5, T/X: LCS failure.
DECEMBER 13, 14, 2017 BOD5, T/X: Improper dilution.
DECEMBER 13, 14, 15, 16, 17, 18, 2017 CL: Technician lacked DOC and no co-signer was used.
DECEMBER 30, 2017, NO2+NO3-N: Sample MS recovery failed, but LCS passed.